 NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2017/05/31
Section 23 64 26 – Rotary-Screw Water Chillers
Page 1 of 6

Part 1 General

1.1 RELATED SECTIONS

.1 Section 01 33 00 – Submittal Procedures.

.2 Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

.3 Section 01 78 00 – Closeout Submittals.

.4 Section 03 30 00 – Cast-in-Place Concrete. 

1.2 REFERENCES
.1 Air-Conditioning and Refrigeration Institute (ARI)

.1 ARI 550/590, Water Chilling Packages Using the Vapor Compression Cycle.

.2 Canadian Standards Association (CSA International)

.1 CSA B52, Mechanical Refrigeration Code.

.3 Environment Canada, (EC)/Environmental Protection Services (EPS)

.1 EPS 1/RA/2, Code of Practice for Elimination of Fluorocarbons Emissions from Refrigeration and Air Conditioning Systems.

.4 Province of Newfoundland and Labrador Boiler, Pressure Vessel and Compressed Gas Regulations.

1.3 SHOP DRAWINGS

.1 Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

.2 Indicate:

.1 Equipment including connections, piping and fittings, valves, strainers, control assemblies and ancillaries, identifying factory and field assembled.

.2 Wiring as assembled and schematically.

.3 Dimensions, construction details, recommended installation procedures and support, mounting bolt hole sizes and locations and point loads.

.4 Type of refrigerant used.

1.4 CLOSEOUT SUBMITTALS

.1 Provide operation and maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

.2 Data to include:

.1 Description of equipment giving manufacturers name, type, model, year, capacity and serial numbers.

.2 Provide part load performance curves.

.3 Details on operation, servicing and maintenance.

.4 Recommended spare parts list.

1.5 delivery, storage and handling
.1 Waste Management and Disposal:

.1 Separate waste materials for reuse and recycling in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal 

.2 Remove from site and dispose of packaging materials at appropriate recycling facilities.

.3 Collect and separate for disposal paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

.4 Divert unused metal and wiring materials from landfill to metal recycling facility as approved by Owner.

1.6 EXTRA MATERIALS

.1 Furnish following spare parts: circuit board, relays, fuses, pilot lights, filters, solenoid hold coils, and thermal expansion valves.  One of each type and size. 
Part 2 Products

2.1 GENERAL

.1 Provide complete air or water cooled screw type chiller package as specified including: compressor; evaporator; condenser, motor and motor starter; controls; control centre; piping; wiring; refrigeration and oil change; ready for connection to chilled water circuit, condenser water circuit, interlocks, and electric power source, installed in welded steel frame with heavy gauge panels and access doors finished to manufacturers standard.

2.2 CAPACITY

.1 Certified ratings based on ARI 550:

.1 Capacity: as indicated.

.2 Water cooled condenser capacity: as indicated.

.3 Air cooled condenser capacity: as indicated.

.4 Power input, including electrical components: as indicated.

.5 Fouling factor: 0.00025.

.6 Refrigerant: R134 a. 

.2 Unit power input capable of operating with line voltage of 575 V,3 PH, 60 Hz.

2.3 COMPRESSOR

.1  Hermetic or Semi-hermetic screw design operating at 3600 r/min.

.2 Unloaded start with capacity modulation by continuous linear modulation of slide valve in response to load change.

.3 Compressor to include suction and discharge shut-off valves; oil sight glass; separate circuit crankcase heater; and unloading device, internal oil filtration, internal pressure relief to suction, high oil temperature protection, loss of oil charge protection, low oil flow protection, suction inlet, screen, electrically activated variable and step unloaders, rubber in shear isolator mountings, full factory oil change.  

.4 Provide nameplate to show capacity at design temperature, type of refrigerant used and total weight in system.

.5 Include 5 year warranty. 

2.4 COMPRESSOR MOTOR

.1 Motor to be suction gas cooled and suitable for voltage of 575 +10%.  Each motor to have one sensor in each motor winding to provide over temperature protection. 

2.5 EVAPORATOR

.1 Dual circuited, direct expansion, shell and tube design with seamless internally finned copper tubes roller expanded into tube sheets.  Evaporator to be designed, tested and stamped in accordance with ASME pressure vessel code for refrigerant side working pressure of 2068 kPa, and water side working pressure of 1482 kPa.  One water pass c/w internal baffles.   Each shell to contain temperature sensors to provide leaving water temperature control, freezestat protection and low refrigerant temperature protection.  Shell also to have vent and drain connections, and be insulated with 20 mm thick flexible elastomeric insulation with RSI value of 0.53 m2 - 0C/W.

2.6 CONDENSER

.1 Water cooled:

.1 Steel shell and copper tube, removable heads, pressure relief device, purge and charge cock and liquid shut-off valve to CSA B52.

.2 Water regulating valve: sensing condensing or head pressure to control water flow.

.2 Air cooled:

.1 Aluminum fins mechanically bonded to seamless copper tube, pressure tested to 3.1 MPa, complete with nitrogen holding charge. 

.2 Direct driven, steel or aluminum propeller type fan, statically and dynamically balanced.  Motor with overload protection, permanently lubricated ball bearings, 575 V. 

.3 Unit panels, structural elements and control boxes constructed of minimum 12 gauge galvanized steel and mounted on a welded structural galvanized steel base.  Unit panels and control boxes to be finished with baked on enamel paint suitable for a harsh marine type environment.

.4 Each unit to have two independent refrigeration circuits.

.5 Condenser controls to be housed in a weathertight enclosure.

.6 Power connections to include main 575/3/60 power and 115/1/60 power for controls.

.7 Condenser coils to have corrosion protective epoxy coating suitable for marine environment.

2.7 OIL Cooler

.1 Provide a brazed plate refrigerant cooler suitable for marine environment.

2.8 CONTROLS

.1 All controls, including sensors, are to be factory mounted and tested prior to shipment.   Microcomputer controls to provide all control functions including start-up and shut down, leaving chilled water temperature control, compressor and electronic expansion valve modulation, anti-cycle logic, automatic lead/lag compressor starting, load limiting and condenser fan staging.  The controller also to provide control outputs for the chilled water pump.

.2 Unit protective functions to include loss of chilled water flow, evaporator freezing, high and low refrigerant pressure, reverse rotation, compressor starting and running over current, phase loss, phase imbalance, phase reversal, and loss of oil flow.

.3 The controls package to include digital cycle counters and hour meters for each compressor, under/over voltage protection, remote alarm contacts, compressor run indication contacts, maximum capacity contacts, percent volts display, and a percent rated amps (each compressor) display. 

.4 A menu driven, digital display to provide a full array of operating conditions and diagnostic readouts.

.5 Unit controls to include adaptive control technology to sense the unit control variables and take corrective action to keep the chiller running when any of the variables approach a limiting or alarm condition.  Abnormal conditions include high/low temperatures and motor current overload.  Should the abnormal condition continue until a protective limit is reached, the unit shall shut down.

.6 Single point power connection to unit complete with non-fused disconnect switch.  Provide control circuit transformer as required.

.7 Provide control panel with a BACnet building automation system communication interface to permit bi-directional communications between chiller control panels and building EMCS for complete monitoring and control of all chiller features and parameters.

Part 3 Execution

3.1 GENERAL

.1 Install unit as indicated, to manufacturer’s recommendations, and in accordance with EPS 1/RA/2.

.2 Ensure adequate clearances for servicing and maintenance. In accordance with manufacturers recommendations.

.3 Provide seasonal start ups and shut downs during warranty period. 

3.2 Commissioning

.1 Manufacturer to approve installation, to supervise startup and to instruct operators. Refer to Section 01 91 13.13 – Commissioning (Cx) Requirements.
.2 Final commissioning to take place between July and September when ambient temperature is at design conditions.

END OF SECTION

Ver. 10/22

