# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 78 00 - Closeout Submittals.

### Section 23 05 48 - Vibration and Seismic Controls for HVAC Piping and Equipment.

## REFERENCES

### American Society for Testing and Materials International, (ASTM)

#### ASTM A153/A153M, Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware.

### Cooling Technology Institute (CTI), (formerly Cooling Tower Institute)

#### CTI ATC-105, Acceptance Test Code for Water Cooling Towers: Mechanical Draft, Natural Draft Fan Assisted Types, and Evaluation of Results, Addendum-1, For Thermal Testing of Wet/Dry Cooling Towers.

#### CTI STD-201, Certification Standard for Commercial Water Cooling Towers.

### Underwriters Laboratories of Canada (ULC)

#### CAN/ULC-S102, Surface Burning Characteristics of Building Materials and Assemblies.

## SHOP DRAWINGS

### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

### Indicate:

#### Connections, piping and fittings, valves, strainers, control assemblies and ancillaries, identifying factory and field assembled.

#### Wiring as assembled and schematically.

#### Dimensions, construction details, recommended installation and support, mounting bolt hole sizes and locations and point loads.

#### Vibration and seismic control measures.

#### Manufacturer's recommended clearances.

## CLOSEOUT SUBMITTALS

### Provide operation and maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

### Include:

#### Description of equipment giving manufacturers name, type, model, year, capacity.

#### Start-up and commissioning procedures.

#### Details of operation, servicing and maintenance.

#### Recommended spare parts list.

## waste management and disposal

### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect, separate and place in designated containers for reuse and recycling, paper, plastic, polystyrene, corrugated cardboard, packaging steel, metal, plastic in accordance with Waste Management Plan.

### Unused sealant materials must not be disposed of into sewer system, into streams, lakes, onto ground or in other location where it will pose health or environmental hazard.

### Fold up metal banding, flatten and place in designated area for recycling.

## EXTRA MATERIALS

### Furnish following spare parts: bearings.

# Products

## GENERAL

### Factory assembled or field erected induced draft crossflow vertical or horizontal, as indicated, discharge cooling tower.

## PERFORMANCE

### Performance: certified in accordance with CTI STD-201.

### Capacity: as indicated.

### Pressure drop through distribution headers and nozzles: as indicated.

### Electrical: maximum full load running amps as indicated.

### Drift loss: maximum 0.05 % of water circulated.

### Sound pressure level measured at 3.0 m: as indicated.

## SIZE AND WEIGHT

### Dimensions: as indicated.

### Operating weight: as indicated.

## MATERIALS

### Steel: hot-dip galvanized to ASTM A153, after fabrication.

### Fibre glass reinforced plastic (FRP).

### Polyvinyl chloride, (PVC): with flame spread rating of 10, smoke developed of 25, to CAN/ULC-S102.

### Wood: pressure treated fir.

### Stainless steel: type 304.

### Plastic: polypropylene.

## CASING AND FRAMEWORK

### Galvanized steel sheet, angles and channels or lap jointed FRP, galvanized angles, channels or FRP casing and fir framing members.

### Structure: designed for wind loads of 1.6 kPa on any projected area and transmission of loads to anchorage.

### Access doors and/or panels: on both end walls for servicing and maintenance.

### Fan deck: galvanized steel pipe perimeter hand and knee rails.

### Access ladder.

## COLD WATER BASIN

### Self draining, with depressed sump with fill, drain, overflow and cleanout connections, anti-vortexing device, strainer, overflow, float operated brass makeup valve.

### Materials: galvanized steel or FRP.

## HOT WATER DISTRIBUTION BASIN

### Open gravity type: galvanized steel or FRP with plastic distribution/metering devices, easily removable for servicing.

## FILL, ELIMINATORS AND LOUVRES

### Fill: PVC vertical sheets or chevron configuration.

### Eliminators: galvanized sheet steel or multipass PVC or PVC integral with fill.

### Louvres: sight tight, galvanized sheet steel or PVC, integral with fill.

## FANS

### Propeller type with adjustable or fixed pitch cast aluminum blades or hollow core, glass reinforced epoxy blades, discharging from galvanized steel or glass reinforced polyester fan cylinders.

### Drive: right angle gear reducer through galvanized steel drive shaft with rubber bushed yokes or V-belt designed for not less than 150% of motor nameplate rating.

### Motor: multi-speed drip proof, ball bearings, weather protected.

#### Locate motor outside moist air stream.

### Drives, fans, and moving parts: protected by galvanized wire guards.

## ACCESSORIES

### Immersion heaters in collection basin: to maintain water temperature at 5 oC when outside temperature is minus 17 oC and wind velocity is 25 kmh. Or remote sump as indicated.

### Immersion thermostat and float control: to operate heaters on low temperature when basin is filled.

### Temperature controller: sensor in collection basin to cycle fans.

### Time delay relay: to limit fan motor starts to not more than 6 /h.

### Capacity control: for stable operation down to 10% of specified capacity at specified wet bulb temperature.

### Manually selected summer/winter switch time delay relays as indicated to:

#### Limit fan motor start-up in reverse rotation during de-ice of inlet louvers.

#### Allow fan to stop and run (in reverse) for preset time.

### Vibration cut-out switch: de-energize fan motors upon excessive vibration.

### Control panel: NEMA 4X to contain:

#### Unfused disconnect switch.

#### Combination motor controllers.

#### Electric alternator.

#### Interlocks and relays.

#### Pilot lights and push buttons.

## VIBRATION ISOLATORS

### To Section 23 05 48 - Vibration and Seismic Controls for HVAC Piping and Equipment.

# Execution

## GENERAL

### Mount on structural supports and vibration isolators as indicated and to manufacturer's recommendations.

### Ensure clearance for servicing and maintenance as recommended by manufacturer.

## commissioning

### Manufacturer's field service representative to approve installation, to supervise start up and to instruct operators.

### Test under actual operating conditions in accordance with CTI ATC-105 to verify specified performance.

### Manufacturer’s representative to be on site to approve installation and startup and commissioning in accordance with Section 01 91 13.13 –Commissioning (Cx) Requirements.

END OF SECTION