# General

## SUMMARY

### Materials and installation for self-contained multizone and single zone, gas, electric, hot water and refrigeration packaged rooftop HVAC units.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements

### Section 01 45 00 – Quality Control

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 01 78 00 – Closeout Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 23 08 02 – Cleaning and Startup of Mechanical Piping Systems

## References

### American National Standards Institute (ANSI)/Air Conditioning and Refrigeration Institute (ARI)

#### ANSI/ARI 210/240, Unitary Air-Conditioning and Air-Source Heat Pump Equipment.

#### ARI 270, Sound Rating of Outdoor Unitary Equipment.

### ANSI/UL 1995 B, Standard for Heating and Cooling Equipment.

### Canadian Standards Association (CSA)

#### CSA B52, Mechanical Refrigeration Code.

#### CSA C22.1, Canadian Electrical Code.

### Health Canada / Workplace Hazardous Materials Information System (WHMIS)]

#### Safety Data Sheets (SDS)

### National Roofing Contractors Association (NRCA)

### National Fire Protection Association (NFPA)

#### NFPA 90A, Installation of Air Conditioning and Ventilating Systems.

### American Bearing Manufacturer’s Association (ABMA)

#### ANSI/ABMA 9 Load Ratings and Fatigue Life for Ball Bearings

#### ANSI/ABMA 11 Load Ratings and Fatigue Life for Roller Bearings.

### Air Movement and Control Association (AMCA)

#### AMCA 300 Reverberaut Room Method for Sound Testing of Fans.

### National Electrical Manufacturer’s Association (NEMA)

#### NEma mg1 Motors and Generators

#### NEMA ICS 7-1 Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable Speed Drive Systems.

### Provincial Boiler, Pressure Vessel and Compressed Gas Regulations.

## SUBMITTALS

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet for packaged rooftop HVAC units.

### Submit WHMIS SDS in accordance with Section 01 33 00 - Submittal Procedures. Indicate VOC's for adhesive and solvents during application and curing.

### Shop Drawings:

#### Submit shop drawings to indicate project layout and dimensions; indicate:

##### Equipment, piping, and connections, together with valves, strainers, control assemblies, thermostatic controls, auxiliaries and hardware, and recommended ancillaries which are mounted, wired and piped ready for final connection to building system, its size and recommended bypass connections.

##### Piping, valves, fittings shipped loose showing final location in assembly.

##### Control equipment shipped loose, showing final location in assembly.

##### Complete internal panel pneumatic tube piping and wiring and external panel pneumatic tube piping and wiring, both as schematics and as actually assembled.

##### Dimensions, internal and external construction details, recommended method of installation with proposed structural steel support, mounting curb details, sizes and location of mounting bolt holes; include mass distribution drawings showing point loads.

##### Detailed composite wiring diagrams for control systems showing factory installed wiring and equipment on packaged equipment or required for controlling devices of ancillaries, accessories, controllers.

##### Pump and fan performance curves.

##### Details of vibration isolation.

##### Estimate of sound levels to be expected across individual octave bands in dB referred to A rating.

##### Type of refrigerant used.

### Test Reports: submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties.

### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

### Instructions: submit manufacturer's installation instructions.

### Manufacturer's Field Reports: manufacturer's field reports specified.

### Closeout submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals include data as follows:

#### Indicate: brief description of unit, indexed, with details of function, operation, control, and service for components.

#### Provide for units, manufacturer's name, type, year, number of units, and capacity.

## QUALITY ASSURANCE

### Pre-Installation Meetings:

#### Convene pre-installation meeting one week prior to beginning work of this Section and on-site installations.

##### Verify project requirements.

##### Review installation and substrate conditions.

##### Co-ordination with other building subtrades.

##### Review manufacturer's installation instructions and warranty requirements.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## DELIVERY, STORAGE AND HANDLING

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan (WMP).

#### Separate for reuse and recycling and place in designated containers steel, metal, plastic waste in accordance with Waste Management Plan (WMP).

#### Handle and dispose of hazardous materials in accordance with Canadian Environmental Protection Act (CEPA), Transportation of Dangerous Goods Act (TDGA), Regional and Municipal, regulations.

#### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

## WARRANTY

### Contractor hereby warrants that packaged rooftop HAVC units and refrigeration compressors will function and operate in accordance with GC 31.1, but for 24 months.

# Products

## General

### Roof mounted, self-contained single zone unit with electric heating elements or hot water coil and DX refrigeration and bear label of CSA.

### Units to consist of cabinet and frame, supply fan, control, air filter, refrigerant cooling coil, compressor, condenser coil and fans, motorized outside air damper, return damper, motorized  exhaust damper.

### Prefabricated roof curb to conform to requirements of National Roofing Contractors Association (NRCA), minimum height 450 mm.

### Conform to ANSI/ARI 210/240, rating for unit larger than 40 kW nominal.

## CabineT

### Cabinets: weatherproofing tested and soundproofing tested to ARI 270, dbA at 3 m free field.

### Framing and supports: 2 mm thick welded steel, galvanized after manufacture, with lifting lugs at top of unit and/or fork lift slots at bottom.

### Outer casing: weathertight galvanized steel with baked enamel finish, to Section 09 91 13 - Exterior Painting.

### Access: removable gasketted hinged doors or panels with locking door handle type or screwdriver operated flush cam type fasteners.

### Insulation: neoprene coated glass fiber on surfaces, 50 mm thick, 32 kg/m3density.

## Fans

### Centrifugal, forward curved impellers, backward inclined, or airfoil, statically and dynamically balanced. Multi V-belt drive with adjustable variable pitch motor pulley, rubber spring isolated hinge mounted motor fan, and motor integrally mounted on isolation base, separated from unit casing with flexible connections and spring isolators. Vibration isolators: 95% efficiency.

## Air Filters

### 50 mm thick, 30 % efficiency, metal framed, replaceable media or throwaway.

### To meet NFPA 90A, air filter requirements type Class 1 or type Class 2.

## Electric Heaters

### Nickel chromium electric resistant type, 64.6 kW/m 2 – stage maximum density at 2.5 m/s.

### Controls:

#### Panel board with multi- stage or modulating SCR controller.

#### Indicating light centre.

#### Remote thermostats as indicated.

#### Fuseblocks (one per step unless otherwise specified).

#### Built-in control transformer.

#### Thermal cut outs: manual reset disc types, one per circuit, one linear bulb type automatic reset.

#### Built-in un-fused disconnect switch.

#### Elements control: accessible with protection against no air flow, short and grounds, and of self checking type.

#### High limit temperature control: de-energize heating elements to protect against over heating.

#### Supply fan: start before electric elements are energized and continue operating until temperature reaches minimum setting. Include switch for continuous fan operation.

#### Conform to Canadian Electrical Code CSA C22.1.

## Hot Water Coil

### Aluminum fins, mechanically bonded to copper tubes.

### Piping: complete with shut off valves, drain valves, unions or flanges.

### Hydrostatically tested to 1.7 MPa.

## Refrigeration

### Conform to CSA B52 and ANSI/UL 465 requirements.

### Compressor/condenser section:

#### Semi-hermetic or hermetic compressors, vibration isolated with flexible suction and discharge connections, oil sight glass, oil pressure switch, crankcase heater, and automatic pump down system with control to liquid line solenoid valve.

#### Fans: propeller type with single piece spun venturi outlets and zinc plated guards. Motors shall be sequenced for head pressure control.

#### Electrical system shall have operating controls, oil and refrigerant pressure protection, motor overload protection, weatherproof electrical wiring with weatherproof, rain tight disconnect.

#### Include refrigerant piping with, sight glass, filter drier and valves.

#### Condenser: staggered copper tube, aluminum fin coil assembly with sub-cooling rows to provide 6 0C sub-cooling.

#### Capacity reduction:  cylinder unloading. Provide flooding for head pressure control for low ambient operation down to 0 0C ambient temperature.

#### Refrigerant: R 134a.

### Evaporator:

#### Rated to ANSI/ARI 210/240.

#### Thermostatic expansion valve, with adjustable super heat and external equalizer.

#### Coil: NPS 1/2 or NPS 5/8 od staggered seamless copper tubes expanded into aluminum fins and insulated condensation pan.

#### Cooling coil condensate drain pans: designed to avoid standing water, to be easily cleaned or removable for cleaning. Drain connection to have deep seal trap and be complete with trap seal primer.

## Controls

### In addition to safety controls, provide smoke sensors in return to NFPA standards, low limit on supply and freeze protection on water coils.

### Single zone cooling control:

#### Zone sensor or room thermostat to activate cooling relay in control circuit cycling compressor. Provide safeties and pressure controls. Condenser fans to operate in sequence.

#### When call for cooling is satisfied, relay is de-energized closing liquid line solenoid valve and pumps down. On two compressor units provide separate circuits to evaporator and condenser.

### Mixed air single zone unit:

#### Motorized outside, return and automatic power exhaust or gravity, relief dampers with spring return damper operator and control package to automatically vary outside air quantity. Outside air and exhaust air dampers, normally closed.

#### Tight fitting opposed blade dampers with neoprene or suitable gaskets, bronze or synthetic bushings and 1% maximum leakage.

#### Damper operation: 24V, spring return motor with gear train sealed in oil, and heater for operation under minus 180C.

#### Mixed air controls: maintain 13 0C mixed air temperature, lock out compressor below 140C ambient, restart 170C.

### Single Zone Heat-Cool Unit

#### Low voltage, adjustable room thermostat controls, heater stages in sequence with delay between stages, compressor and supply fan shall maintain room temperature setting.

#### Thermostat: include system selector switch day-night, heat-cool-auto-off and fan control switch (on-auto).

#### Mixed air controls: maintain 13 0C mixed air temperature, lock out compressor below 140C ambient, restart 170C.

### Night mode: unit cycles as unit heater with 100% recirculation on winter cycles.

### Night set-back: 15 o C.

## Remote panel

### Provide remote readout panel for each unit containing:

#### Signal lights indicating system status, heating system failure cooling system failure and dirty filters.

#### Check switches proving signal light operation.

#### System on-off switch.

#### Fan on-off switch.

#### Manual 6 h timer to override night-set back control.

### Provide gauges in remote panel indicating outside air, mixed air, return air and discharge air temperatures for each deck before heat exchangers.

## Capacity

### Capacity:  see schedule.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install as per manufacturers' instructions on roof curbs provided by manufacturer.

### Manufacturer’s representative to certify installation, supervise start-up and commission unit.

### Run drain line from cooling coil condensate drain pan to discharge over roof.

## FIELD QUALITY CONTROL

### Manufacturer's Field Services:

#### Have manufacturer’s representative of products supplied under this Section review work involved in handling, installation/application, protection and cleaning of its products, and submit written reports, in acceptable format, to verify compliance of work with Contract.

#### Provide manufacturer's field services, consisting of product use recommendations and periodic site visits for inspection of product installation, in accordance with manufacturer's instructions.

#### Schedule site visits to review work at stages listed:

##### After delivery and storage of products, and when preparatory work on which work of this Section depends is complete, but before installation begins.

##### Twice during progress of work at 25% and 60% complete.

##### Upon completion of work, after cleaning is carried out.

### Obtain reports within three (3) working days of review and submit immediately to Owner.

### Verify accessibility, serviceability of components including motorized dampers, filters coils, fans, motors, operators, humidifiers, sensors, electrical disconnects.

### Verify accessibility, cleanability, drainage of drain pans for coils, humidifiers.

### Performance Verification:

#### General:

##### In accordance with Section 23 08 02 - Cleaning and Start-up of Mechanical Piping Systems, supplemented as specified herein.

#### Rooftop Air Handling Units:

##### Set zone mixing dampers for full cooling, except that where diversity factor forms part of design set that % of zone dampers to full heating.

##### Set outside air and return air dampers for minimum outside air.

##### Set face and bypass dampers so face dampers are fully open and bypass dampers are fully closed.

##### Check for smooth, vibrationless correct rotation of supply fan impeller.

##### Measure supply fan capacity.

##### Adjust impeller speed as necessary and repeat measurement of fan capacity.

##### Measure pressure drop for each component of air handling unit.

##### Set outside air and return air dampers for the % of outside air required by design and repeat measurements of fan capacity.

##### Reduce differences between fan capacity at minimum and maximum outside air less than 5 %.

##### Set face and bypass dampers to full bypass and repeat measurement of fan capacity.

##### Reduce difference between fan capacity with F&BPD fully closed to bypass and fully open to bypass to less than 5 %.

##### Reduce difference between fan capacity at full cooling and fan capacity at full heating to less than 5 %.

##### OAD: verify for proper stroking, interlock with RAD.

##### Measure DBT, WBT of SA, RA, EA.

##### Measure air cooled condenser discharge DBT.

##### Measure flow rates (minimum and maximum) of SA, RA, EA, relief air.

##### Simulate maximum cooling load and measure refrigerant hot gas and suction temperatures and pressures.

##### Use smoke test to verify no short-circuiting of EA, relief air to outside air intake or to condenser intake.

##### Simulate maximum heating load and:

###### Verify temperature rise across heat exchanger.

###### Perform flue gas analysis. Adjust for peak efficiency.

###### Verify combustion air flow to heat exchanger.

###### Simulate minimum heating load and repeat measurements.

##### Measure radiated and discharge sound power levels under maximum heating demand and under maximum cooling demand with compressors running.

##### Verify operating control strategies, including:

###### Heat exchanger operating and high limit.

###### Early morning warm-up cycle.

###### Freeze protection.

###### Economizer cycle operation, temperature of change-over.

###### Alarms.

###### Voltage drop across thermostat wiring.

###### Operation of remote panel including pilot lights, failure modes.

##### Set zone mixing dampers for full heating and repeat measurements.

##### Measure leakage past zone mixing dampers by taking temperature measurements. Reduce leakage to less than 5 %.

##### Measure return fan capacity.

##### Adjust impeller speed as necessary and repeat measurement of return fan capacity.

##### Check capacity of heating unit.

##### Measure DX refrigeration system performance as specified Section.

##### Refer to other sections of these specifications for PV procedures for other components.

#### Start-Up:

##### General: in accordance with Section 23 08 02 - Cleaning and Start-up of Mechanical Piping Systems.

#### Verify accessibility, serviceability of components including motorized dampers, filters, coils, fans, motors, operators, humidifiers, sensors, electrical disconnects.

#### Verify accessibility, clean ability, drainage of drain pans for coils, humidifiers.

### Commissioning Reports:

#### In accordance with Section 01 91 13.13 - Commissioning (Cx) Requirements: reports supplemented as specified herein. Include:

##### Report forms as specified Section 01 91 13.13 - Commissioning (Cx) Requirements: Report Forms and Schematics.

## DEMONSTRATION

### Training: in accordance with Section 01 91 13.13 - Commissioning (Cx) Requirements: Training of O&M Personnel, supplemented as specified.

## CLEANING

### Perform cleaning operations as specified in Section 01 74 00 – Cleaning and in accordance with manufacturer's recommendations.

### On completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION