# General

## RELATED SECTIONS

### Section 01 33 00 – Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 23 09 33 – Electric and Electronic Control System for HVAC.

### Section 26 05 00 – Common Work Results - Electrical.

## PRODUCT DATA

### Submit product data in accordance with Section 01 33 00 - Submittal Procedures.

### Product data to include:

#### Replacement data for motor element, thermostat and switch.

#### Mounting methods.

#### kW rating, voltage, phase.

#### Cabinet material thicknesses.

#### Physical size.

#### Finish.

#### Thermostat, transformer, controls where integral.

## waste management and disposal

### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal, and with the Waste Reduction Workplan.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal and wiring materials from landfill to metal recycling facility approved by Owner.

# Products

## FORCED AIR HEATERS

### Forced air heaters, wall mounted commercial type as follows:

#### Enclosure:

##### Steel, 1.2 mm thick.

##### Knockouts for 19 mm diameter conduit left, right, bottom and rear.

##### Grill and frame finished coating.

#### Elements and Fan:

##### Mineral insulated.

##### Motor: totally enclosed, shaded pole, impedance protected motor.

### Controls:

#### Wall mounted thermostat: type low voltage, to Section 23 09 33 - Electric and Electronic Control System for HVAC.

#### Built-in tamperproof controls. 'On-Off-Fan Only' selector switch and temperature control knob.

### Capacity as indicated.

# Execution

## INSTALLATION

### Install heaters in accordance with manufacturer's instructions.

### Make power and control connections.

## COMMISSIONIING

### Perform tests in accordance with Section 26 05 00 – Common Work Requirements - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION