# General

## SUMMARY

### Section includes:

#### Materials and installation for electrical incremental heating and cooling units and accessories.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements.

### Section 01 45 00 – Quality Control

### Section 01 74 21 – Construction / Demolition Waste Management and Disposal.

### Section 01 78 00 – Closeout Submittals.

### Section 23 09 33 – Electric and Electronic Control System for HVAC.

### Section 26 05 00 – Common Work Results - Electrical.

## references

### Health Canada / Workplace Hazardous Materials Information System (WHMIS)]

#### Safety Data Sheets (SDS)

### American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE)

#### ASHRAE 58 – Method of Testing for Rating Room Air Conditioner and Packaged Terminal Air Conditioning Heating Capacity.

## submittals

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

#### Method of Testing for Rating Room Air-Conditioner and Packaged Terminal Air-Conditioning Heating Capacity.

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet for electric incremental heating and cooling units and accessories.  Include information as follows:

##### Replacement data for motor element, thermostat and switch.

##### Mounting methods.

##### kW rating.

##### Cabinet material thicknesses.

##### Physical size.

##### Finish.

##### Cabinet surface temperature.

##### Thermostat, transformer, controls where integral.

##### Installation instructions.

#### Submit WHMIS SDS in accordance with Section 01 33 00 - Submittal Procedures. Indicate VOC's for adhesive and solvents during application and curing.

### Test Reports: submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties.

### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

### Instructions: submit manufacturer's installation instructions.

### Manufacturer's Field Reports: manufacturer's field reports specified.

### Closeout submittals: submit maintenance and engineering data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## quality assurance

### Pre-Installation Meeting:

#### Convene pre-installation meeting one week prior to beginning work of this Section and on-site installations.

##### Verify project requirements.

##### Review installation and substrate conditions.

##### Co-ordination with other building subtrades.

##### Review manufacturer's installation instructions and warranty requirements.

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## DELIVERY, STORAGE AND HANDLING

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan (WMP).

#### Separate for reuse and recycling and place in designated containers steel, metal, plastic waste in accordance with Waste Management Plan (WMP).

#### Handle and dispose of hazardous materials in accordance with Canadian Environmental Protection Act (CEPA), Transportation of Dangerous Goods Act (TDGA), Regional and Municipal, regulations.

#### Divert unused metal materials from landfill to metal recycling facility as approved by Owner.

# Products

## Heating/Cooling Units

### Housing:

#### Wall box: 1.2 mm thick, zinc coated.

#### Supply air grille anodized finish extruded aluminum.

#### Cabinetry: 1.2 mm thick.

#### Acoustic lining.

#### Interior cabinet panel: 1.2 mm thick baked enamel paint, complete with supply grille.

#### Manually-controlled fresh air damper.

### Major Components:

#### One or Separate permanent split phase capacitor motors for condensing and evaporator section.

#### Compressor.

#### Electric Heating Coil.

#### Condenser Fan.

### Controls:

#### Silent operating relays for fan, compressor and heater.

### Unit Capacities: as indicated.

#### Cooling capacity based on 35°C DB and 19°C WB.

### Compressor sealed, internally spring mounted, vibration isolated.

### Electric Coil:

#### Helix wound nichrome heating coils.

#### Incoloy sheathed elements.

### Prewired for connection to a single receptacle or outlet box.

### Condenser fan centrifugal or propeller, evaporator fan, dual speed centrifugal.

### Controls:

#### Thermostat: unit mounted or remote as indicated.

#### Pushbuttons: Off, High, Medium, Low, Cool, Heat, Unit Open, Unit Closed.

### Washable air filters arranged for easy removal.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install in accordance with manufacturer's written instructions.

### Make power and control connections.

### Ensure positive contact between condenser frame and exterior louvre to prevent cross- ventilation of supply and discharge air.

## cleaning

### Perform cleaning operations as specified in Section and in accordance with manufacturer's recommendations.

### On completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

## commissioning

### Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Set controls and operate each unit.

### Take readings and record:

#### Current.

#### Air velocity at discharge.

#### Discharge air temperature.

END OF SECTION