# General

## summary

### Section Includes:

#### Materials and application of electric duct heaters.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 35 29.06 – Health and Safety Requirements

### Section 01 35 43 – Environmental Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements

### Section 26 05 00 – Common Work Results - Electrical.

## references

### Canadian Standards Association (CSA International)

#### CSA C22.2 No.155, Electric Duct Heaters.

### Department of Justice Canada (Jus.)

#### Canadian Environmental Protection Act (CEPA)

### Transport Canada (TC)

#### Transportation of Dangerous Goods Act (TDGA)

## submittals

### Make submittals in accordance with Section 01 33 00 – Submittal Procedures.

### Submit product data and include:

#### Element support details.

#### Heater:  total kW rating, voltage, phase.

#### Number of stages.

#### Rating of stage:  rating, voltage, phase.

#### Heater element watt/density and maximum sheath temperature.

#### Maximum discharge temperature.

#### Physical size.

#### Unit support.

#### Performance limitations.

#### Clearance from combustible materials.

#### Internal components wiring diagrams.

#### Minimum operating airflow.

#### Pressure drop, operating and minimum airflow.

#### Controller type.

#### Accessories included.

## quality assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## delivery, storage, and handling

### Waste Management and Disposal:

#### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Remove from site and dispose of packaging materials at appropriate recycling facilities.

#### Collect and separate for disposal, paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

#### Place materials defined as hazardous or toxic in designated containers in accordance with Section 01 35 43 – Environmental Procedures.

#### Handle and dispose of hazardous materials in accordance with CEPA, TDGA, Regional and Municipal regulations.

#### Ensure emptied containers are sealed and stored safely.

#### Fold up metal and plastic banding, flatten and place in designated area for recycling.

# Products

## Duct Heaters

### Duct heaters: flange type or insert type.

### To carry CSA Approval, and listed for zero clearance to combustibles.

### Elements:

#### Open coil elements of nickel-chrome resistance wire.

#### Coils machine crimped into stainless steel terminals extending at least 25mm into the air stream.

#### All terminal hardware shall be stainless steel.

#### Coils shall be supported by ceramic bushings staked into the supporting brackets.

### Frames: Heater frames and boxes shall be corrosion resistant steel.

### Terminal box:

#### NEMA 1 general purpose enclosure.

#### Hinged, latching cover.

#### Multiple concentric knockouts to accept field wiring.

#### Terminal blocks to accommodate field wiring.

#### All internal wiring to be complete with 105ºC rated insulation.

### Ratings:

#### Heaters to be rated for voltage, phase, and KW capacity as indicated in schedule on drawings.

#### All three phase heaters to have equal, balanced, three phase stages.

#### Supply heaters with size and quantity of fixed and proportional heating stages as indicated in schedule.

### Controls:

#### Factory mounted and wired in control box. Use terminal blocks for power and control wiring.

#### Controls to include:

##### Magnetic contactors.

##### Fixed differential pressure switch.

##### Manual and automatic reset high limit.

##### Control transformers.

##### Solid state relays.

##### Door interlocked disconnect switch (non-fused).

##### HRC load fuses.

##### Controller type to be as indicated in the duct heater schedule or on Control drawings as follows:

###### Proportional Control: single-stage proportional control providing full modulation of the heater capacity with a silicon controlled rectifier (SCR) suitable for control input of 0 – 10 VDC or 4-20mA.

###### Hybrid Control: multiple On-Off stages combined with one proportional modulating silicon controlled rectifier (SCR) stage suitable for control input of 0 – 10 VDC or 4-20mA.

##### Heater to be controlled by 0 – 10 VDC or 4-20mA remote control signal from the building automation system supplied and installed by the EMCS Contractor.

##### Airflow Providing Switch: diaphragm type air pressure switch with automatic reset, screw type setpoint adjustment and static pressure probe; switch to de-energize duct heater circuits in case of insufficient air flow.

### Performance: see schedule.

### Provide heater complete with protective screens on inlet/outlet.

# Execution

## Installation

### Make power and control connections in accordance with CSA C22.2 No.46.  Install in accordance with manufacturer’s instructions.

### Locate duct heater in accordance with manufacturer's minimum recommended distances for operation, service access and unit removal.

### Provide additional hangers and supports in accordance with Section 23 05 29 - Hangers and Supports for HVAC Piping and Equipment where duct heater weight cannot be supported solely by existing duct.

### Make power and control connections to CSA C22.2 No.155.

### Verify that ductwork and casings are free of debris before operating and testing duct heaters.

## COMMISSIONING

### Perform tests in accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements and Section 26 05 00 – Common Work Results – Electrical.

END OF SECTION