# General

## summary

### Section includes:

#### Materials and installation for fan coil units.

## Related Sections:

### Section 01 33 00 – Submittal Procedures.

### Section 01 74 21 – Construction / Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 23 09 33 – Electric and Electronic Control System for HVAC.

### Section 26 05 00 – Common Work Results – Electrical

## references

### Health Canada / Workplace Hazardous Materials Information System (WHMIS)]

#### Safety Data Sheets (SDS)

### American Society of Heating, Refrigeration and Air-Conditioning Engineers (ASHRAE)

#### ASHRAE 79 – Method of Testing for Rating Fan-Coil Conditioners.

## submittals

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

##### Product data to include:

###### Filters, fan accessibility.

###### Suspension, anchoring of cabinet.

###### Physical size.

###### Thermostat, transformer, controls where integral.

###### Finish.

###### kW rating, voltage, phase.

###### Cabinet material thicknesses.

### Shop Drawings:

#### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

## QUALITY ASSURANCE

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## DELIVERY, STORAGE, AND HANDLING

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

#### Divert unused metal and wiring materials from landfill to metal recycling facility approved by Owner.

# Products

## fan coil Units

### Cabinet: steel, 1.2 mm thick, floor wall or ceiling mounting, recessed. Front inlet/front outlet.

### Elements: stainless steel sheathed with corrosion protected aluminum fins covering full length of element capacity as indicated.

### Blower motors: one speed, single phase.

### Built-in thermostat with integral relay as indicated. Wall mounted thermostats: type as indicated, to Section 23 09 33 - Electric and Electronic Control System for HVAC.

### Fan delay switch.

### On-Off switch (for wall mount unit only).

### Two position selector switch (for wall mount unit only).

### Fresh air duct adapter.

### Filter: washable and reusable.

### Trim for flush installation.

### Finish: three stage phosphatized treatment followed by 2 coats baked enamel with final coat.

### Assembly fully wired to one outlet location.

### Multiple knockouts for up to 38 mm diam conduit.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Mount or hang units as indicated.

### Make power and control connections.

### Co-ordinate ducting of fresh air with other Divisions at floor.

## commissioning

### Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

## Cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION