# General

## summary

### Section Includes:

#### Cabinet convector heaters, controls and installation.

## Related Sections

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 23 09 33 – Electric and Electronic Control System for HVAC.

### Section 26 05 00 – Common Work Results - Electrical.

## References

### Canadian Standards Association (CSA)

#### CSA C22.2 No.46, Electric Air-Heaters.

### Health Canada/Workplace Hazardous Materials Information System (WHMIS)

#### Safety Data Sheets (SDS).

## submittals

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

#### Submit product data sheets for cabinet convector heaters. Include:

##### Product characteristics.

##### Performance criteria.

##### Mounting methods.

##### Physical size.

##### kW rating, voltage, phase.

##### Cabinet material thicknesses.

##### Limitations.

##### Colour and finish.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

### Closeout Submittals:

#### Submit operation and maintenance data for cabinet convector heaters in accordance with Section 01 78 00 - Closeout Submittals

## quality assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29 06 - Health and Safety Requirements.

## delivery, storage, and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## Cabinet Convector Heaters

### Wall mounted cabinet: to CSA C22.2 No.46, pre-drilled back for securing to wall:

#### Bottom inlet/top outlet.

#### Bottom inlet/front outlet.

#### Front inlet/front outlet.

#### Front inlet/top outlet.

#### Front panel: 1.6 mm thick, steel.

#### Finish: phosphatized and finished with 2 coats baked enamel, beige colour.

### Elements: mineral insulated with steel sheath and welded fins, secured and free-floating for expansion.

### Floor drop-in cabinet: to CSA C22.2 No.46.

#### Cabinet: 1.6 mm thick steel, flanged to rest on finished floor.

#### Element: mineral insulated.

#### Sheath: steel.

#### Vanes: continuously welded helical, mounted on baffle for removable as unit.

#### Finish: phosphatized and finished with 2 coats baked enamel, beige colour.

#### Grille: drop-in type, stainless steel finish, designed for easy removal.

## Controls

### Wall mounted thermostats: type line, low voltage or electronic, Energy Star certified, to Section 23 09 33 – Electric and Electronic Control System for HVAC or Section 25 30 02 – EMCS: Field Control Devices as indicated.

### Built-in thermostat: 1 or 2 pole with tamperproof screws and cover and auxiliary relays, transformer as indicated in Heating Fixtures Schedule located on drawings.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install cabinet convectors as indicated.

### Locate floor drop-in heaters not closer than 150 mm from wall. For 350 mm units, fit between floor joists. For larger units frame- in as indicated. Flange of heater case must rest on finished floor. Fix rigidly with wood screws.

### Install wall mounted thermostats in locations indicated.

### Make power and control connections.

## cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

## commissioning tests

### Perform tests in accordance with Section 26 05 00- Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION