# General

## summary

### Section includes:

#### Base board and finned tube radiation, and cabinet convectors including installation.

## Related Sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal

### Section 01 78 00 – Closeout Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

## References

### Health Canada / Workplace Hazardous Materials Information System (WHMIS)]

#### Safety Data Sheets (SDS)

### Hydronic Institute of Boiler and Radiator Manufacturers (IBR)

### Air-Conditioning, Heating and Refrigeration Institute (AHRI)

## submittals

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures.  Include product characteristics, performance criteria, and limitations.

#### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Material Safety Data Sheets (MSDS) in accordance with Section 01 33 00 - Submittal Procedures.

### Shop Drawings:

#### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

#### Indicate:

##### Equipment, capacity, piping, and connections.

##### Dimensions, internal and external construction details, recommended method of installation with proposed structural steel support, sizes and location of mounting bolt holes.

##### Special enclosures.

### Samples:

#### Submit samples in accordance with Section 01 33 00 - Submittal Procedures.

#### Submit 1200 mm length sample enclosure showing method of securing to structure and connecting to adjacent length of enclosure.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

### Closeout Submittals:

#### Submit maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## quality assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## delivery, storage, and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## Dampers

### Factory built, internal damper, at enclosure air outlet grille for each convection type heating unit not thermostatically controlled. Refer to schedules on drawings.

## Capacity

### As indicated, based on 88oC average water temperature, 11oC temperature drop and 18oC at entering air temperature.

## Finned Tube Radiation

### Heating elements: NPS 3/4, 1,  1 1/4 sized to maintain minimum 0.9 m/s velocity, seamless copper tubing as indicated, 1.2 mm minimum wall thickness, mechanically expanded into flanged collars of evenly spaced aluminum fins, 100 x 100 mm nominal, 130 fins per metre suitable for sweat fittings.

### Heating elements: NPS 1 1/4 steel as indicated, tube sized to maintain minimum 0.9 m/s velocity, 3.1 mm minimum wall thickness, mechanically expanded into flanged collars of evenly spaced steel fins 100 x 100 mm nominal fins, 105 fins per metre.

### Element hangers: ball bearings or sliding guide rod cradle type providing unrestricted longitudinal movement on enclosure brackets. Space brackets 900 mm centres maximum.

### Standard enclosures: 1.3 mm thick steel complete with components for wall-to-wall or complete with die formed end caps having no knock-outs, with inside corners, outside corners, as indicated. Provide full length channel and sealer strip at top of wall edge. Height as indicated. Joints and filler pieces to be flush with cabinet. Support rigidly top and bottom, on wall mounted brackets. Joints and filler pieces to be clear of grilles located to provide easy access to valves and vents. Provide access doors for valves, vents, traps. Finish cabinet with factory applied baked primer coat.

### Special enclosures: as indicated.

### Dimensions for enclosures: measure site conditions. Do not scale from drawing.

### Provide for noiseless expansion of all components.

## CABINET CONVECTORS

### Heating element: seamless copper tubing mechanically expanded into flanged collars of evenly spaced aluminum fins and cast iron headers, steel side plates and supports.

### Cabinet: type as indicated, 1.6 mm thick steel front and top panels, exposed corners rounded, secured removable front panel, braced and reinforced for stiffness. Provide access doors for valves, vents, traps. Finish cabinet with factory applied baked primer coat.

### Catalogue rating: certified commercial standard to AHRI.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install in accordance with manufacturer's instructions.

### Install in accordance with piping layout and reviewed shop drawings.

### Provide for pipe movement during normal operation.

### Maintain sufficient clearance to permit performance of service maintenance.

### Check final location with Owner if different from that indicated prior to installation. Should deviations beyond allowable clearances arise, request and follow Owner’s directive.

### Valves

#### Install valves with stems upright or horizontal unless approved otherwise.

#### Install isolating gate or ball valves on inlet and balancing valves on outlet of each unit as indicated

### Venting:

#### Install screwdriver vent on cabinet convector, terminating flush with surface of cabinet.

#### Install automatic air vent on continuous finned tube radiation.

### Clean finned tubes and comb straight.

### Install flexible expansion compensators as indicated.

## Cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

## commissioning

### Commissioning in accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements.

### END OF SECTION