# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 02 62 00.01 – Hazardous Materials.

## REFERENCES

### Air Movement and Control Association (AMCA).

#### AMCA 210.  Laboratory Methods of Testing Fans for Aerodynamic Performance Rating.

### Natural Electrical Manufacturers Association (NEMA).

#### NEMA MG-1 Motors and Generators

### Canadian Standards Association (CSA).

## PRODUCT DATA

### Submit product data in accordance with Section 01 33 00 - Submittal Procedures.

### Submit WHMIS MSDS – Safety Data Sheets in accordance with Section 01 33 00 - Submittal Procedures. WHMIS acceptable to Labour Canada, and Health Canada.

### Submit product data sheets for unit heaters.  Include:

#### Product characteristics.

#### Performance criteria.

#### Mounting methods.

#### Physical size.

#### kW rating, voltage, phase.

#### Cabinet material thicknesses.

#### Limitations.

#### Colour and finish.

### Manufacturer's Instructions: Provide to indicate special handling criteria, installation sequence, cleaning procedures.

## SHOP DRAWINGS

### Submit shop drawings in accordance with Section 01 33 00 - Submittal Procedures.

### Indicate:

#### Equipment, capacity and piping connections.

#### Dimensions, internal and external construction details, recommended method of installation with proposed structural steel support, sizes and location of mounting bolt holes.

## CLOSEOUT SUBMITTALS

### Provide operation and maintenance data for unit heaters for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

## WASTE MANAGEMENT AND DISPOSAL

### Separate and recycle waste materials in accordance with Section 01 74 21 – Construction/Demolition Waste Management and Disposal, and with Waste Reduction Workplan.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect and separate for disposal paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal and wiring materials from landfill to metal recycling facility approved by Owner.

### Fold up metal banding, flatten and place in designated area for recycling.

### Collect, package and store existing unit heaters for either reuse, recycling or rebuilding and return to recycler in accordance with Waste Management Plan.

# Products

## CABINET UNIT HEATERS

### Cabinet type: surface semi-recessed or recessed as indicated, 1.6 mm thick steel with rounded exposed corners and edges, removable panels, glass fibre insulation and integral air outlet and inlet.

### Finish with factory applied primer coat.

### Special cabinets or front panels: as indicated.

### Coils: aluminum fins mechanically bonded to copper tubes as indicated. Hydrostatically tested to 1 MPa.

### Electric coils as indicated: nickel-chrome resistance coils embedded in refractory material and enclosed in steel sheathing with low or high watt density extended fins.

#### Two stage heating with magnetic contactors, high temperature limit switch, and fan override switch.

#### Control heating elements in conjunction with fan by common control switch.

### Fans: centrifugal double width wheels, statically and dynamically balanced, direct driven, sleeve bearings, resilient mounted.

### Motor: multi-speed, tapped wound permanent split capacitor type with sleeve bearings, built-in thermal overload protection and resilient rubber isolation mounting.

### Filters: removable 25 mm thick fibrous glass throwaway or permanent washable type.

### Capacity: as indicated.

### Control:

#### 3 speed on-off switch with integral overloads in cabinet or wall mounted as indicated.

#### Low limit aquastat strapped on to steam or hot water heating supply set to prevent fan operating below 27 oC.

#### Control thermostat: See Section 23 09 33 – Electric and Electronic Control System for HVAC or Section 25 30 02 – EMCS:  Field Control Devices as indicated.

## HORIZONTAL UNIT HEATERS

### Casing: 1.6 mm thick cold rolled steel, gloss enamel finish, with threaded connections for hanger rods.

### Coils: seamless copper tubing, silver brazed to steel headers with evenly spaced aluminum fins mechanically bonded to tubing. Hydrostatically test to 1 MPa.

### Fan: direct drive propeller type, factory balanced, with anti-corrosive finish and fan guard.

### Motor: speed as indicated continuous duty, built-in overload protection, and resilient motor supports.

### Air outlet: two-way adjustable louvres.

### Capacity as indicated, base steam capacity on 14 kPa, base hot water heating capacity on 8 o C E.W.T. and 11o C temperature drop, 15o C - E.A.T.

### Control:

#### 3 speed on-off switch with integral overloads in cabinet or wall mounted as indicated.

#### Low limit aquastat strapped on to steam or hot water heating supply set to prevent fan operating below 27 o C.

#### Control thermostat: See Section 23 09 33 – Electric and Electronic Control System for HVAC or Section 25 30 02 – EMCS:  Field Control Devices as indicated.

## VERTICAL UNIT HEATERS

### Casing: 1.6 mm thick cold rolled steel, glossed enamel finish, with threaded connections for hanger rods.

### Coils: seamless copper tubing, silver brazed to steel headers and with evenly spaced aluminum fins mechanically bonded to tubing. Hydrostatically test to 1 MPa.

### Fan: direct drive propeller type, factory balanced, with anti-corrosive finish.

### Motor: speed as indicated, continuous duty, ball bearing motor with built-in overload protection, and resilient motor supports.

### Air outlet: adjustable multi-vane diffuser with finish to match casing, as indicated.

### Capacity: as indicated, base steam capacity on 14 kPa, base hot water heating capacity on 88o C  E.W.T. and 11o C temperature drop, 15 o C - E.A.T.

### Control:

#### 3 speed on-off switch with integral overloads in cabinet or wall mounted as indicated.

#### Low limit aquastat strapped on to steam or hot water heating supply set to prevent fan operating below 27o C.

#### Control thermostat: See Section 23 09 33 – Electric and Electronic Control System for HVAC or Section 25 30 02 – EMCS:  Field Control Devices as indicated.

# Execution

## INSTALLATION

### Install in accordance with manufacturer's instructions.

### Provide double swing pipe joints as indicated.

### Check final location with Owner if different from that indicated prior to installation.

#### Should deviations beyond allowable clearances arise, request and follow Owner’s directive.

### Hot water units: for each unit, install gate or ball valve on inlet as indicated and calibrated balancing valve on outlet of each unit. Install drain valve at low point.

#### Install manual or automatic air vent at high point as indicated.

### Steam units: for each unit, install gate valve on inlet, steam trap assembly as indicated on outlet.

### Clean finned tubes and comb straight.

### Provide supplementary suspension steel as required.

### Install thermostats in locations indicated.

### Before acceptance, set discharge patterns and fan speeds to suit requirements.

## COMMISSIONING

### Commissioning in accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION