# General

## RELATED SECTIONS

### Section 01 33 00 – Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 23 09 33 – Electric and Electronic Control System for HVAC.

### Section 26 05 00 – Common Work Results - Electrical.

## PRODUCT DATA

### Submit product data in accordance with Section 01 33 00 - Submittal Procedures.

### Show mounting methods and reflector details.

## waste management and disposal

### Separate and recycle waste materials in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal, and with the Waste Reduction Workplan.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect and separate for disposal paper, plastic, polystyrene, corrugated cardboard, packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal and wiring materials from landfill to metal recycling facility approved by Owner.

# Products

## INFARED RADIANT HEATERS

### Type 1:  Ceiling mount type

#### High density radiant panel heater designed for lay-on installation in suspended imperial t-bar ceiling system.

#### Plaster frame for flush installation in gypsum board ceilings where required.

#### Unit constructed of min 24 ga corrosion resistant steel with radiant surface finished on high emmissivity textured latex acrylic paint.  Assembly to incorporate insulation mass on back of heating element.

#### Heating element to be alloy resistance wire with 200o C insulation.

### Type 2:  Under slab/earth mass type

#### Radiant heating panel shall be factory fabricated electric heating panels consisting of a low-temperature alloy resistance heating wire embedded in approximately 6 mm thick gypsum board and electrically insulated with a special compound rated for 200o C.  Each panel shall have a watt density range of 430 to 516 watt/m2 when energized on 347 volts.  Panels to be complete with cold leads for connection to circuit conductors using self-stripping electrical tap connectors and screw-on enclosure for waterproofing and protection.

#### The installed system shall carry a written 10 year warranty.

## CONTROLS

### Thermostat and solid state relays:  to Section 23 09 33 – Electric and Electronic Control System for HVAC, or Section 25 30 02 – EMCS: Field Control Devices rating as indicated.

# Execution

## INSTALLATION (TYPE 1)

### Install infrared heaters and controls as indicated and in accordance with manufacturer's instructions.

### Ensure that manufacturer's mounting instructions for each fixture, including minimum distances from ceiling, walls or combustible materials, are followed.

### Make power and control connections.

### Recessed units in suspended acoustic tile ceilings are to be independently supported from the building structure, not from the suspended ceiling grid.

## Installation (TYPE 2)

### Install heating panels as indicated and in accordance with manufacturer’s instructions.

### Run conductors between panels. To ceiling mounted junction boxes.  Mark circuits as indicated with indelible markers.

### Connect panel leads to circuit conductors using self-stripping connectors.

### Avoid sharp 90 bends at end of run.

### Space cable minimum of 50 mm from corners or other metal.

### Do not cross or bunch cables.  At least 40 mm clearance must be maintained between cables at all times.

### Connect heating circuits to wall mounted thermostats and solid state relays as indicated.

## commissioning

### Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

### With all circuits connected and prior to waterproofing and sealing, perform resistance tests on each circuit with an ohmmeter.  Measured resistance must equal calculated resistance using the following formula:

Resistance (ohms)  = (Design voltage)2

Total Wattage

### Recheck all connections and re-do as necessary until measured resistance is equal to calculated resistance.

### Waterproof and seal all connections according to manufacturer’s instructions.

### Recheck resistance measurements to ensure resistance is the same as previously measured.

### Notify Owner immediately if any discrepancy is found.

### Check and confirm satisfactory operation of radiant heating system.

## QUALIFIED INSTALLER

### The entire installation, wiring and testing shall be done by the factory trained installer.

END OF SECTION