# General

## summary

### Section includes:

#### Snow melting cables, accessories, thermostat and snow sensing controls, and installation.

## Related Sections

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 23 09 33 – Electrical and Electronic Control System HVAC.

### Section 26 05 00 – Common Work Results - Electrical.

## References

### Canadian Standards Association (CSA International)

#### CAN/CSA C22.2 No. 130, Requirements for Electrical Resistance Heating Cables and Heating Device Sets.

### Health Canada / Workplace Hazardous Materials Information System (WHMIS)]

#### Safety Data Sheets (SDS)

## submittals

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

### Closeout Submittals:

#### Submit operation and maintenance data for heating cable in accordance with Section 01 78 00 - Closeout Submittals

#### Record on drawings, layout of snow melting cables in poured concrete, hot mastic asphalt, free air.  Indicate depth of cable where applicable.

## quality assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## delivery, storage, and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

## Warranty

### Contractor hereby warrants that snow melting heating cables will operate as specified in accordance with GC 31.1, but for 24 months.

# Products

## General

### Heating cables: to CSA C22.2 No. 130.1, CSA C22.2 No. 130.2.

## Snow Melting Cables

### Mineral insulated copper conductor with stainless steel sheath and HDPE jacket factory spliced and sealed, cold leads, and as indicated.

### Copper alloy conductor with X-linked/PVC nylon insulation, copper ground braid, PVC protective jacket factory spliced and sealed cold leads, and as indicated.

### Self-limiting type cable.

## Heating Cables with Attachment Plug Cap

### Heating cable sets with U-ground attachment plug cap for indoor and outdoor use with X-link polyethelene insulated conductor and lead sheath cover. Cable length and voltage as indicated.

## Accessories

### Galvanized steel prepunched strapping to hold cables in place when embedded in concrete or asphalt.

### Roof clips to hold cables in place when installed on roof.

### Steel wire mesh: 2.6 mm diam on 100 mm centres for use with cables embedded in asphalt.

## Controls

### Thermostat: type line voltage, Energy Star certified, remote bulb type, rating as indicated, to Section 23 09 33 – Electric and Electronic Control System for HVAC or Section 25 30 02 – EMCS: Field Control Devices.

## Snow Sensing Controls

### Snow sensing controls consisting of control unit and sensor module.

### System features as follows:

#### Lowering of outside air temperature to selected dial setting to close contacts of variable thermal control in control unit and activate solid state module.

#### Thermal control in sensor module, responsive to outer surface temperature, to control heater to maintain temperature above freezing point.

#### Snow falling on heated sensor module to melt, allowing sufficient current to close magnetic relay and complete circuit to control unit output lines, energizing cable installation.

#### Control unit complete with manual off-auto control switch, pilot light, and manual temperature setting switching device.

#### Control module rating: 120 V ac, 5 A.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install cables in accordance with manufacturer's instructions.

### If two pour method is used, install cable straps fastened to concrete with 25 mm nails. Locate at 0.9 m intervals.

### Secure cable to anchoring devices and confine cable within 150 mm minimum from edge of slab.

### Protect heating cables with 13 mm plywood sheets and remove progressively when concrete topping is poured.

### Install steel mesh anchoring system when hot mastic asphalt topping is installed, and secure cables to underside of wiring mesh.

### Do not cross expansion joints with cable. Where structural design changes location of expansion joints, affecting snow melting cables, report to Owner.

### Do not alter heating cable length.

### Ensure cables do not bunch or cross.

### Do not energize cable for 28 days after concrete pour.

### Make power and control connections.

## Field Quality Control/ commissioning

### Perform tests in accordance with Section 26 05 00 – Common Work Results – Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Use 500 V megger to test cables for continuity and insulation value and record readings as follows:

#### On cable reel.

#### After installation.

#### Before concrete or asphalt pouring.

#### During concrete or asphalt pouring.

#### 24 h after pouring.

### Where resistance of 50 megohms or less is measured, stop work and advise Owner.  Replace cable as necessary.

## cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION