# General

## summary

### Section Includes:

#### Floor warming cables, accessories, controls, and installation.

## Related Sections

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 23 09 33 – Electric and Electronic Control System for HVAC

### Section 26 29 10 – Motor Starters to 600V.

## References

### Canadian Standards Association (CSA International)

#### CAN/CSA C22.2 No. 130, Requirements for Electrical Resistance Heating Cables and Heating Device Sets.

### Health Canada / Workplace Hazardous Materials Information System (WHMIS)]

#### Safety Data Sheets (SDS)

## submittals

### Product Data:

#### Submit manufacturer's printed product literature, specifications and datasheet in accordance with Section 01 33 00 - Submittal Procedures. Include product characteristics, performance criteria, and limitations.

##### Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS) in accordance with Section 01 33 00 - Submittal Procedures.

### Quality assurance submittals: submit following in accordance with Section 01 33 00 - Submittal Procedures.

#### Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Instructions: submit manufacturer's installation instructions.

### Closeout Submittals:

#### Submit operation and maintenance data for heating cable in accordance with Section 01 78 00 - Closeout Submittals

#### Record layout of cables in poured-in-place concrete, hot mastic asphalt, indicating depth of cables.

## quality assurance

### Health and Safety:

#### Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

## delivery, storage, and handling

### Packing, shipping, handling and unloading:

#### Deliver, store and handle in accordance with manufacturer's written instructions and Section 01 61 00 - Common Product Requirements.

### Waste Management and Disposal:

#### Construction/Demolition Waste Management and Disposal: separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

# Products

## Floor Warming Heating Cables

### Heating cables: to CSA C22.2 No. 130.1, CSA C22.2 No. 130.2.

### Mineral insulated copper conductor with copper sheath and HDPE jacket factory spliced and sealed cold leads.

### Copper alloy conductor with X-link polyethylene insulation, copper ground braid, PVC caps, protective jacket, factory spliced and sealed cold leads.

## Accessories

### Galvanized steel prepunched strapping to hold cables in place when embedded in concrete or asphalt.

### Steel wire mesh 2.6 mm thick on 100 mm centres for use with cables embedded in asphalt.

## Controls

### Thermostat: type line voltage electronic , Energy Star certified , remote bulb type, rating as indicated, to Section 23 09 33 - Electric and Electronic Control System for HVAC or Section 25 30 02 – EMCS: Field Control Devices as indicated.

### Contactors: Type 1, to Section 26 29 10 – Motor Starters to 600 V, rating as indicated.

# Execution

## manufacturer’s instructions

### Compliance: comply with manufacturer's written recommendations or specifications, including product technical bulletins, handling, storage and installation instructions, and datasheet.

## Installation

### Install heating cable in accordance with manufacturer's instructions.

### Secure cable straps to concrete with 25 mm nails. Strapping located 1m intervals.

### Secure cable to anchoring devices and confine cable within 50 mm minimum from edge of slab.

### Do not penetrate waterproofing membrane.

### Protect heating cables with 13 mm plywood sheets and remove progressively when concrete topping is poured.

### Place remote sensing bulb in conduit in between heating cables 50 mm deep in concrete.

### Do not cross expansion joints with cable.

### Do not alter heating cable length.

### Ensure cables do not bunch or cross.

### Do not energize cable for 28 days after concrete topping.

### Ground cable and mesh to building grounding system.

### Fasten floor warming cable to underside of slab on 400 mm centres.

### Make power and control connections.

## Field Quality Control/Commissioning

### Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Use 500 V megger to test cables for continuity and insulation value and record readings as follows:

#### On cable reel.

#### After installation.

#### Before concrete casting.

#### During concrete casting.

#### 24 hours after casting.

### Where resistance of 50 megohms or less is measured, stop work and advise Owner.  Replace cable as required.

## cleaning

### Proceed in accordance with Section 01 74 00 - Cleaning.

### Upon completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.

END OF SECTION