# General

## SUMMARY

### Section Includes.

#### Requirements and procedures for identification of devices, sensors, wiring, tubing, conduit and equipment, for building Energy Monitoring and Control System (EMCS) Work and nameplates, materials, colours and lettering sizes.

## Related Sections

### Section 01 33 00 - Submittal Procedures.

### Section 25 05 01 - EMCS: General Requirements.

## REFERENCES

### Canadian Standards Association (CSA International).

#### CSA C22.1, The Canadian Electrical Code, Part I, Safety Standard for Electrical Installations.

## DEFINITIONS

### For acronyms and definitions refer to Section 25 05 01 - EMCS: General Requirements.

## SYSTEM DESCRIPTION

### Language Operating Requirements: provide identification for control items in English.

## SUBMITTALS

### Submittals in accordance with Section 01 33 00 - Submittal Procedures and Section 25 05 02 – EMCS:  Submittals and Review Process supplemented and modified by requirements of this Section.

### Submit to Owner for approval samples of nameplates, identification tags and list of proposed wording.

# Products

## NAMEPLATES FOR PANELS

### Identify by plastic laminate, 3 mm thick melamine, matt white finish, black core, square corners, lettering accurately aligned and engraved into core, mechanically attached with self-tapping screws.

### Sizes: 25 x 67 mm minimum.

### Lettering: minimum 7 mm high, black.

### Inscriptions: machine engraved to identify function.

## NAMEPLATES FOR FIELD DEVICES

### Identify by plastic encased cards attached by plastic tie.

### Sizes: 50 x 100 mm minimum.

### Lettering: minimum 5 mm high produced from laser printer in black.

### Data to include: point name and point address, make, model number.

### Companion cabinet: identify interior components using plastic enclosed cards with point name and point address.

## NAMEPLATES FOR ROOM SENSORS

### Identify by stick-on labels using point identifier.

### Location: as directed by Owner.

### Letter size: to suit, clearly legible.

## WARNING SIGNS

### Equipment including motors, starters under remote automatic control: supply and install orange coloured signs warning of automatic starting under control of EMCS.

### Sign to read:  "Caution: This equipment is under automatic remote control of EMCS" as reviewed by Owner.

## WIRING

### Supply and install numbered tape markings on wiring at panels, junction boxes, splitters, cabinets and outlet boxes.

### Colour coding: to CSA C22.1.  Use colour coded wiring in communications cables, matched throughout system.

### Power wiring: identify circuit breaker panel/circuit breaker number inside each EMCS panel.

## PNEUMATIC TUBING

### Numbered tape markings on tubing to provide uninterrupted tracing capability.

## CONDUIT

### Colour code EMCS conduit.

### Pre-paint box covers and conduit fittings.

### Coding: use fluorescent orange paint and confirm colour with Owner during "Preliminary Design Review".

# Execution

## NAMEPLATES AND LABELS

### Ensure that manufacturer's nameplates, CSA labels and identification nameplates are visible and legible at all times.

## EXISTING PANELS

### Correct existing nameplates and legends to reflect changes made during work.

END OF SECTION