NL Master Specification Guide

for Public Funded Buildings
Section 26 05 00 – Common Work Results
Re-Issued 2021/05/31
 - Electrical
Page 1 of 18

General

1.1 General

.1 This Section covers items common to Sections of Division 26. This section supplements requirements of Division 1, Division 23, Division 27, Division 28, Division 33 and Division 34. 
1.2 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CSA C22.1, Canadian Electrical Code, Part 1, Safety Standard for Electrical Installations.
.2 CAN/CSA-22.3 No. 1, Overhead Systems.
.3 CAN3-C235, Preferred Voltage Levels for AC Systems, 0 to 50,000 V.

1.3 Care, Operation and Start-up

.1 Instruct Owner and operating personnel in the operation, care and maintenance of systems, system equipment and components.
.2 Operating instructions to include following:

.1 Wiring diagrams, control diagrams, and control sequence for each principal system and item of equipment.
.2 Start up, proper adjustment, operating, lubrication, and shutdown procedures.

.3 Safety precautions.

.4 Procedures to be followed in event of equipment failure.

.5 Other items of instruction as recommended by manufacturer of each system or item of equipment.
.3 Arrange and pay for services of manufacturer's factory service engineer to supervise start-up of installation, check, adjust, balance and calibrate components and instruct operating personnel.

.4 Provide these services for such period, and for as many visits as necessary to put equipment in operation, and ensure that operating personnel are conversant with all aspects of its care and operation.

1.4 design requirements
.1 Operating voltages: to CAN3-C235 

.2 Motors, electric heating, control and distribution devices and equipment to operate satisfactorily at 60 Hz within normal operating limits established by above standard. Equipment to operate in extreme operating conditions established in above standard without damage to equipment.
1.5 SUBMITTALS

.1 Submit drawings stamped and signed by professional engineer registered or licensed in Province of Newfoundland and Labrador, Canada.

.2 Submit wiring diagrams and installation details of equipment indicating proposed location, layout and arrangement, control panels, accessories, piping, ductwork, and other items that must be shown to ensure coordinated installation.

.3 Identify on wiring diagrams circuit terminals and indicate internal wiring for each item of equipment and interconnection between each item of equipment.

.4 Indicate of drawings clearances for operation, maintenance, and replacement of operating equipment devices.
.5 Quality Control: in accordance with Section 01 45 00 - Quality Control.
.1 Provide CSA certified equipment and material. Where CSA certified equipment and material is not available, submit such equipment and material to authority having jurisdiction for approval before delivery to site.
.2 Submit test results of installed electrical systems and instrumentation.

.3 Submit, upon completion of Work, load balance report as described in sentence 3.4.6.
.4 Submit certificate of acceptance from authority having jurisdiction upon completion of Work to Owner.

.6 Manufacturer's Field Reports: submit to Owner within seven (7) working days of review, verifying compliance of Work and electrical system and instrumentation testing, as described in paragraph 3.6- FIELD QUALITY CONTROL.
.7 Single Line Electrical Diagrams
.1 Provide single line electrical diagrams in glazed frames as follows:

.1 Electrical distribution system: locate in main electrical room.

.2 Electrical power generation and distribution systems: locate in power plant rooms.

.2 Provide fire alarm riser diagram, plan and zoning of building in glazed frame at fire alarm control panel and annunciator.

.3 Drawings: 600 x 600 mm minimum size.
.8 The electrical contractor shall supply an arc-flash study of the building’s entire distribution system, to be performed by the successful electrical equipment supplier. The contractor shall furnish the supplier with distances, wire lengths and transformer shop drawings as required. Supply also stick-on labels for all equipment, identifying the arc-flash hazard rating of each distribution board and panel board. Such labelling shall meet CSA Z462. Supply one full set of Personal Protective Equipment required for each identified hazard rating in the arc-flash study. The arc-flash study shall be submitted with the electrical distribution equipment shop drawings. The electrical distribution equipment shop drawings will not be reviewed until the arc-flash study is received. Refer to Section 26 05 73 – Power Systems Studies for further details.
.9 Shop Drawings:

.1 Indicate details of construction, dimensions, capacities, weights and electrical performance characteristics of equipment or materials.

.2 Where applicable, indicate wiring, single line and schematic diagrams.

.3 Include wiring drawings or diagrams showing interconnection with work of other sections.

.4 Each shop drawing will be stamped and signed by the Contractor before submitting, stating that he has checked the drawings against the requirements as called for in the Contract Documents and also in the case where the equipment is attached to or connects to other equipment, that is has been properly coordinated with this equipment, whether supplied under Division 26 or under other Divisions.

.5 Each shop drawing for non-catalogue items shall be prepared specifically for this project. If brochures are submitted for catalogue items, the brochures shall be marked deficiently indicating the item or items to be supplied.

.6 Work shall not be proceeded with on any of the equipment until final review of shop drawings received by the Contractor.

.7 Shop drawing review is for general compliance with Contract Documents. No responsibility is assumed by the Owner for correctness of dimensions or details. Corrections or comments, or lack thereof, made on the shop drawings during the Owner’s review does not relieve the Contractor from compliance with the requirements of the drawings and specifications.
.1 If changes are required, notify Owner of these changes before they are made.
.10 Operation and Maintenance Data:

.1 Provide operation and maintenance data for incorporation into operation and maintenance manuals. Manuals shall be supplied to Section 01 78 00.
.2 Include in operations and maintenance data:
.1 Details of design elements, construction features, component function and maintenance requirements to permit effective start-up operation, maintenance, repair, modification, extension and expansion of any portion or feature of installation.
.2 Technical data, product data, supplemented by bulletins, exploded views, technical description of items and part lists. Advertising or sales literature not acceptable.
.3 Wiring and schematic diagrams and performance curves.
.4 Names and addresses of local suppliers for items included in maintenance manuals.
.5 Copy of reviewed shop drawings.
.11 As-Built Drawings: Submit in accordance with 01 78 00 – Closeout Submittals.
1.6 Permits, Fees and Inspection

.1 Submit to Electrical Inspection Division and Supply Authority necessary number of drawings and specifications for examination and approval prior to commencement of work.

.2 Pay associated fees.

.3 Owner will provide drawings and specifications required by Electrical Inspection Division and Supply Authority at no cost.

.4 Notify Owner of changes required by Electrical Inspection Division prior to making changes.

.5 Furnish Certificates of Acceptance from Electrical Inspection Division or authorities having jurisdiction on completion of work to Owner. 

1.7 co-ordination
.1 Co-ordinate work with work of other divisions to avoid conflict.

.2 Locate distribution systems, equipment, and materials to provide minimum interference and maximum usable space.

.3 Locate all existing underground services and make all parties aware of their existence and location.

.4 Where interference occurs, Owner must approve relocation of equipment and materials regardless of installation order.

.5 Notwithstanding the review of shop drawings, this division may be required to relocate electrical equipment which interferes with the equipment of other trades, due to lack of co-ordination by this Division.  The cost of this relocation shall be the responsibility of this Division.  The Owner shall decide the extent of relocation required. 

1.8 CUTTING AND PATCHING

.1 Inform all other divisions in time, concerning required openings.  Where this requirement is not met, bear the cost of all cutting.  Openings of 200 mm or smaller shall be the responsibility of Division 26.  Openings larger than 200 mm shall be the responsibility of Division 1.  Obtain written approval of Structural engineer before drilling any beams or floors.

1.9 PROTECTION

.1 Protect exposed live equipment during construction for personnel safety.

.2 Shield and mark all live parts “LIVE 120 VOLTS”, or with appropriate voltage in English.

.3 Arrange for installation of temporary doors for rooms containing electrical distribution equipment.  Keep these doors locked except when under direct supervision of electrician.

1.10 Record drawings

.1 Obtain and pay for three sets of white prints.  As the job progresses, mark these prints to accurately indicate installed work.  Have the white prints available for inspection at the site at all times and present for scrutiny at each job meeting.

.2 Show on the record drawings the installed inverts of all services entering and leaving the building and the property.  Dimension underground services at key points of every run in relation to the structure and building.

.3 Indicate exact location of all services for future work.  Show and dimension all work embedded in the structure.

.4 Submit record drawings within 30 days prior to start of commissioning.

1.11 INSPECTION OF WORK

.1 The Owner will make periodic visits to the site during construction to ascertain reasonable conformity to plans and specifications but will not execute quality control.  The Contractor shall be responsible for the execution of his work in conformity with the construction documents and with the requirements of the inspection authority. 

1.12 SCHEDULING OF WORK

.1 Work shall be scheduled in phases as per other divisions of the architectural specifications.

.2 Become familiar with the phasing requirements for the work and comply with these conditions.

.3 No additional monies will be paid for contractor’s requirement to comply with work phasing conditions.

1.13 FIRE RATING OF PENETRATIONS

.1 Maintain fire ratings around conduits passing through floors, ceilings and fire rated walls.

.2 Use 3M brand or equal fire barrier products at each penetration.

.3 Acceptable products for fire barrier products shall be 3M #CP25 fire barrier caulk, #303 putty, #FS 195 wrap and #CS195 sheet.
.4 Acceptable manufacturers:  Nelson, Fire Stop Systems, 3M or approved equal. Material of same manufacturer to be used throughout project.
1.14 DELIVERY, STORAGE AND HANDLING
.1 Material Delivery Schedule: provide Owner with schedule within 2 weeks after award of Contract.
1.15 SYSTEM START-UP
.1 Instruct Owner and operating personnel in operation, care and maintenance of systems, system equipment and components.
.2 Arrange and pay for services of manufacturer's factory service engineer to supervise start- up of installation, check, adjust, balance and calibrate components and instruct operating personnel.
.3 Provide these services for such period, and for as many visits as necessary to put equipment in operation, and ensure that operating personnel are conversant will aspects of its care and operation.
1.16 WASTE MANAGEMENT & DISPOSAL
.1 Separate and recycle waste materials in accordance with Division 01.
.2 Remove from site and dispose of all packaging materials at appropriate recycling facilities.
.3 Collect and separate for disposal: paper, plastic, polystyrene and corrugated cardboard packaging material for recycling in accordance with Waste Management Plan.
.4 Divert unused wiring and metal materials from landfill to metal recycling facility as approved by Owner.
.5 Place materials defined as hazardous or toxic waste in designated containers.
.6 Ensure emptied containers are sealed and stored safely for disposal.
.7 Unused materials must not be disposed of into sewer system, streams, lakes, onto ground or in other locations, where it will pose health or environmental hazard.
.8 Do not dispose of preservative treated wood through incineration. Dispose of treated wood, end pieces, wood scraps and sawdust at sanitary landfill approved by Owner.
.9 Divert unused batteries and antifreeze to appropriate recycling facilities as approved by Owner.

1.17 EQUIPMENT SUPPORTS AND HOUSEKEEPING PADS
.1 Equipment supports supplied by equipment manufacturer are specified elsewhere in Division 26.
.2 Fabricate equipment supports not supplied by equipment manufacturer from structural grade steel meeting requirements of Division 5. Submit structural calculations with shop drawings. Ensure that supports meet the requirements of the National Building Code.
.3 Mount base mounted equipment on chamfered edge housekeeping pads, minimum of 100 mm high and 50 mm larger than equipment dimensions all around.
1.18 ANCHOR BOLTS AND TEMPLATES
.1 Supply anchor bolts and templates for installation by other divisions.
1.19 ACCESS DOORS
.1 Supply access doors for concealed electrical equipment to allow operation, inspection, adjusting and servicing.
.2 Use flush mounted 600 x 600 mm for body entry and 300 x 300 mm for hand entry unless otherwise noted. Doors to open 180, have rounded safety corners, concealed hinges, screwdriver latches and anchor straps.
.3 Material:

.1 Use stainless steel with brushed satin or polished finish in special areas such as tiled or marble surfaces and as directed by Owner.
.2 In remaining areas, use prime coated steel.

.3 Use ULC rated access doors in fire rated walls and ceilings.
.4 Installation

.1 Locate so that concealed items are accessible.
.2 Locate so that hand or body entry (as applicable) is achieved.
.3 Installation is specified in applicable sections.

Part 2 Products 
2.1 Electric Motors, Equipment and Controls

.1 Supplier and installer responsibility is indicated on electrical drawings and related mechanical responsibility is indicated on mechanical drawings, where applicable.

.2 Control wiring and conduit is specified in Division 26 except for conduit, wiring and connections below 50 V which are related to control systems specified in Division 25 and shown on mechanical drawings. Division 25 – EMCS Controls Contractor is responsible for all conduit, wiring and connections below 50V which are related to control systems in Division 25 and shall comply with the requirements of Division 26 for standard of quality.
2.2 Materials and Equipment

.1 Provide materials and equipment in accordance with Section 01 61 00 - Common Product Requirements.

.2 Equipment and material to be CSA certified. Where there is no alternative to supplying equipment which is not CSA certified, obtain special approval from Electrical Inspection Division.

.3 Factory assemble control panels and component assemblies.

2.3 Finishes

.1 Shop finish metal enclosure surfaces by application of rust resistant primer inside and outside, and at least two coats of finish enamel.

.1 Paint outdoor electrical equipment "equipment green" finish to EEMAC Y1-1.

.2 Paint indoor switchgear and distribution enclosures light grey to EEMAC 2Y-1.
2.4 Warning Signs

.1 As specified and to meet requirements of Electrical Inspection Department and Owner.

.2  Porcelain enamel decal signs, minimum size 175 x 250 mm.

.3 Install adhesive backed polyester arc flash hazard labels on all major electrical components including the service entrance switchboard, bus duct breakers, panelboards, disconnects, splitters and master control centers/starters. Refer to Section 26 05 73 – Power System Studies for further details.
2.5 Wiring Terminations

.1 Lugs, terminals, screws used for termination of wiring to be suitable for either copper or aluminum conductors.
2.6 Equipment Identification

.1 Identify electrical equipment with nameplates and labels as follows:

.1 Nameplates: Lamicoid 3 mm thick plastic engraving sheet, black white face, black white core, mechanically attached with self tapping screws.
.2 Sizes as follows:
	NAMEPLATE SIZES

	Size 1
	10 x 50 mm
	1 line
	3 mm high letters

	Size 2
	12 x 70 mm
	1 line
	5 mm high letters

	Size 3
	12 x 70 mm
	2 lines
	3 mm high letters

	Size 4
	20 x 90 mm
	1 line
	8 mm high letters

	Size 5
	20 x 90 mm
	2 lines
	5 mm high letters

	Size 6
	25 x 100 mm
	1 line
	12 mm high letters

	Size 7
	25 x 100 mm
	2 lines
	6 mm high letters


.2 Labels:

.1 Embossed plastic labels with 6 mm high letters unless specified otherwise.
.3 Wording on nameplates and labels to be approved by Owner prior to manufacture.

.4 Allow for average of twenty-five (25) letters per nameplate and label.

.5 Identification to be English (and French where applicable). 

.6 Nameplates for terminal cabinets and junction boxes to indicate system name and voltage characteristics.

.7 Disconnects, starters and contactors: indicate equipment being controlled and voltage.

.8  Terminal cabinets and pull boxes: indicate system name and voltage.

.9 Transformers: indicate capacity, primary and secondary voltages and transformer number.

.10 Panelboards: indicate name, voltage, capacity and upstream panel serving mains.
2.7 Wiring Identification

.1 Identify wiring with permanent indelible identifying markings, either numbered or coloured plastic tapes, on both ends of phase conductors of feeders and branch circuit wiring.

.2 Maintain phase sequence and colour coding throughout.

.3 Colour code: to CSA C22.1, Canadian Electrical Code.

.4 Use colour coded wires in communication cables, matched throughout system.

2.8 Conduit and Cable Identification

.1 Colour code conduits, boxes and metallic sheathed cables.

.2 Code with plastic tape or paint at points where conduit or cable enters wall, ceiling, or floor, and at 15 m intervals.

.3 Colours: 25 mm wide prime colour and 20 mm wide auxiliary colour.

	Conduit System
	Prime Color
	Auxiliary Color

	up to 250 V
	Yellow
	

	up to 600 V
	Yellow
	Green

	up to 5 kV
	Yellow
	Blue

	up to 15 kV
	Yellow
	Red

	Telephone
	Green
	

	Other Communication Systems
	Green
	Blue

	Fire Alarm
	Red
	

	Emergency Voice
	Red
	Blue

	Other Security Systems
	Red
	Yellow


2.9 MATERIAL SPECIFIED

.1 Where additional manufacturers are named under Articles entitled "Approved Manufacturers", the selection of a named manufacturer, in reference to a particular article, shall be the Contractor's responsibility.
.2 Materials or products specified without the clauses "or approved equal" or "approved manufacturers" shall be supplied as specified and no proposed substitution will be considered.
.3 Where approvals are granted for the use of other equipment, any and all changes or additions required for the installation or operation of the approved equipment will be made by the Contractor at their own expense and no claims will be approved for any such changes, notwithstanding approval of shop drawings. Equipment that is accepted and installed and then does not perform as represented by original submitted data shall be replaced by the Contractor with equipment as specified at no charge to the Owner.
.4 Trade names are given as a standard of quality and configuration.
2.10 EXAMINATION OF OTHER WORK
.1 This Division requires the examination of the material and work for all other Divisions under which the work of this Section depends for proper completion. Any defect in work, levels or materials shall be reported to the Owner. The work of this Division shall not commence until such defects have been corrected. This also applied to existing work installed under other Contracts.
2.11 CUTTING, PATCHING, SLEEVES AND PLATES
.1 All drilling for hangers, rod, inserts and work of similar nature shall be done by Division 26.
.2 Have core drilled openings installed in foundation walls to accommodate the work of this Division. Seal conduit or cable through the cored opening using industrial duty round compression seals sized to suit diameter of conduit or cable. Cable seals to be Roxtec RS type or approved equal.
2.12 HANGERS AND EQUIPMENT SUPPORTS
.1 All equipment provided under the Electrical Division shall be complete with all necessary supports and hangers required for a safe and workmanlike installation and to avoid strain on conduit, etc. Auxiliary supports where required shall be provided under this Division.
.2 Hammer driven hanger supports, eg. staples, nails, etc. will not be used.
.3 Expansion bolts, inserted after concrete has been poured are acceptable.
.4 Paint all hangers, eg. U-bolts, trapeze hangers, etc. BEFORE INSTALLATION.
.5 Wire is not an acceptable conduit support.
2.13 TESTING, ACCEPTANCE AND GUARANTEE
.1 The work of this Contract shall be tested and installed and any defects in operation shall be remedied immediately. Tests required by local authorities shall be the responsibility of the Contractor. When the work is completed, it shall be tested in its entirety and shall be in good working order before the Owner's Certificate of Acceptance shall be issued.
.2 A written guarantee shall be supplied to the Owner by the Contractor covering the prompt making good of any and all defects in material and workmanship for the period of one (1) year from the date of acceptance and the making good of any such defects shall be completely the responsibility of the Contractor.

Part 3 Execution 

3.1 NAMEPLATES AND LABELS
.1 Ensure manufacturer's nameplates, CSA labels and identification nameplates are visible and legible after equipment is installed.
3.2 location of outlets

.1 Locate outlets in accordance with Section 26 27 26 – Wiring Devices. 

.2 Do not install outlets back-to-back in wall; allow minimum 150 mm horizontal clearance between boxes.

.3 Change location of outlets at no extra cost or credit, providing distance does not exceed 3000 mm, and information is given before installation.

.4 Locate light switches on latch side of doors. Locate disconnect devices in mechanical and elevator machine rooms on latch side of door.
3.3 Conduit and cable installation

.1 Install conduit and sleeves prior to pouring of concrete. Sleeves through concrete: schedule 40 steel pipe, sized for free passage of conduit, and protruding 50 mm.

.2 If plastic sleeves are used in fire rated walls or floors, remove before conduit installation.

.3 Install cables, conduits and fittings to be embedded or plastered over, neatly and close to building structure so furring can be kept to minimum.
3.4 mounting heights

.1 Mounting height of equipment is from finished floor to centreline of equipment unless specified or indicated otherwise.

.2 If mounting height of equipment is not specified or indicated, verify before proceeding with installation.

.3 Install electrical at following heights unless indicated otherwise.

.1 Local switches: 1200 mm.

.2 Wall receptacles:

.1 General: 300 mm.

.2 Above top of continuous baseboard heater: 200mm.

.3 Above top of counters or counter splash backs: 175 mm.

.4 In mechanical rooms: 1400 mm.

.3 Panelboards: as required by Code or as indicated.

.4 Telephone and interphone outlets: 300 mm.

.5 Wall mounted telephone and interphone outlets: 1400 mm.

.6 Fire alarm stations: 1200 mm.

.7 Fire alarm bells: 2400 mm.

.8 Television outlets: 300 mm.

.9 Wall mounted speakers: 2400 mm.

.10 Clocks: 2400 mm.

.11 Door bell pushbuttons: 1200 mm.

.12 Exit lights: 2400 mm.

.13 Emergency lighting heads: 2400 mm.

3.5 Co-ordination of protective devices

.1 Ensure circuit protective devices such as overcurrent trips, relays and fuses are installed to required values and settings.
3.6 FIELD QUALITY CONTROL

.1 All electrical work to be carried out by qualified, licensed electricians or apprentices as per the conditions of the Provincial Act respecting manpower vocational training and qualification. Employees registered in a provincial apprentices program shall be permitted, under the direct supervision of a qualified licensed electrician, to perform specific tasks – the activities permitted shall be determined based on the level of training attained and the demonstration of ability to perform specific duties.

.2 The work of this division to be carried out by a contractor who holds a valid Code 1 Electrical Contractor License as issued by the Province.

.3 Perform tests in Accordance with this section as noted and Section 01 91 13.13 – Commissioning (Cx) Requirements.
.4 Load Balance:

.1 Measure phase current to panelboard with normal loads (lighting) operating at time of acceptance. Adjust branch circuit connections as required to obtain best balance of current between phases and record changes. 

.2 Measure phase voltages at loads and adjust transformer taps to within 2% of rated voltage of equipment.

.3 Submit, at completion of work, report listing phase and neutral currents on panelboards, dry-core transformers and motor control centres, operating under normal load. State hour and date on which each load was measured, and voltage at time of test.

.5 Contractor to conduct and pay for the costs the following tests (Cost of the following tests are not covered in cash allowance amounts identified in Section 01 21 00 – Allowance):

.1 Power generation and distribution system including phasing, voltage, grounding and load balancing.

.2 Circuits originating from branch distribution panels.

.3 Lighting and its control.

.4 Motors, heaters and associated control equipment including sequenced operations of systems where applicable.

.5 Systems: fire alarm system, communications.

.6 Furnish manufacturer’s certificate or letter confirming that entire installation as it pertains to each system has been installed to manufacturer’s instructions.

.7 Insulation resistance testing.

.1 Measure and record circuits, feeders and equipment up to 350 V with a 500 V instrument. 

.2 Measure and record 350 – 600 V circuits, feeders and equipment with a 1000 V instrument. 

.3 Check resistance to ground before energizing and record value.

.8 Carry out tests in presence of Owner.

.9 Provide instruments, meters, equipment and personnel required to conduct tests during and conclusion of project.

.10 Submit test results for Owner’s review and include in Commissioning Manuals specified in Section 01 91 13.13 – Commissioning (Cx) Requirements.

3.7 PREPERATION FOR FIRESTOPPING
.1 Prepare the space between conduits and adjacent sleeve or fire separation for the use of fire proofing material.
.2 Where cables or conduits pass through fire rated walls or ceilings, sleeve with steel conduit and prepare the opening for fire and smoke sealing and seal with proper fire and smoke rated material.
.3 Where conduits pass through fire or smoke rated partitions, install a junction box in the conduit just prior to exiting the space. Use this junction box to install smoke stopping material.
3.8 PAINTING
.1 Apply at least one coat of corrosion resistant primer paint to ferrous supports and site fabricated work.
.2 Prime and touch up marred finished paintwork to match original.
.3 Restore to new condition, finishes that have been damaged too extensively to be primed and touched up.
3.9 TRIAL USAGE
.1 Owner may use equipment and systems for test purposes prior to acceptance. Supply labour, material, and instruments required for testing.
.2 Trial usage to apply to following equipment and systems:
.1 Lighting system.

.2 Power distribution system.

.3 Communication systems.

.4 Security systems.

.5 Metering system.

.6 Fire alarm system.
.7 Public address system.
3.10 TESTS

.1 Give 24 h written notice of date for tests. Conceal work only after testing and approval by Consultant. Conduct tests in presence of Consultant. Bear costs including re-testing and making good.

.2 Equipment: test as specified in relevant sections.

.3 Prior to tests, isolate all equipment or other parts that are not designed to withstand test pressures or test medium.
3.11 DRAWINGS, CHANGES, ACCESSIBILITY

.1 The drawings shall be considered to show the general character and scope of work and not the exact details of the installation.

.2 The installation shall be complete with all supports and accessories required for a complete operative and satisfactory installation.

.3 The location, arrangement and connection of equipment and materials as shown on the drawings represent a close approximation to the intent and requirements of the Contract.

.4 The right is reserved by the Owner to make reasonable changes required to accommodate conditions arising during the progress of the work. Such changes shall be done at no extra cost to the Owner unless the location, arrangement or connection is more than 3.0 m from that shown.

.5 Actual location of existing services shall be verified in the field where necessary before work is commenced.

.6 Changes and modifications necessary to ensure co-ordination and to avoid interference or conflicts with other trades, or to accommodate existing conditions, shall be made at no extra cost to the Owner.

3.12 CLEANING
.1 Clean and touch up surfaces of shop-painted equipment scratched or marred during shipment or installation, to match original paint.
.2 Clean and prime exposed non-galvanized hangers, racks and fastenings to prevent rusting.
.3 Complete final cleaning of equipment and work area as acceptable to Owner.

.4 At time of final cleaning, clean lighting, reflectors, lenses and other lighting surfaces that have been exposed to construction dust and dirt.

END OF SECTION

Ver. 10/22

