NL Master Specification Guide

for Public Funded Buildings
Section 26 05 05 – Selective Demolition 
Issued 2019/09/10
for Electrical
Page 1 of 6

General

1.1 SUMMARY
.1 This Section includes requirements for selective demolition and removal of electrical safety and security, communications components including removal of conduit, junction boxes, and panels to source (home run removal) and incidentals required to complete work described in this Section.
1.2 RELATED REQUIREMENTS

.1 Section 02 41 13– Selective Site Demolition.
.2 Section 02 41 16– Structure Demolition.
.3 Section 02 41 19.16 – Selective Interior Demolition.
.4 Section 02 41 99 – Demolition for Minor Works.

.5 Section 02 82 00.02 – Asbestos Abatement.

1.3 REFERENCES
.1 CSA Group (CSA)
.1 CSA S350 M1980, Code of Practice for Safety in Demolition of Structures
1.4 definations
.1 Demolish: Detach items from existing construction and legally dispose of items off site, unless indicated as removed and salvaged, or removed and reinstalled.

.2 Remove: Planned deconstruction and disassembly of electrical items from existing construction including removal of conduit, junction boxes, cabling and wiring from electrical component to panel taking care not to damage adjacent assemblies designated to remain; legally dispose of items off site, unless indicated as removed and salvaged, or removed and reinstalled.

.3 Remove and Salvage: Detach items from existing construction and deliver them to Owner ready for reuse.

.4 Remove and Reinstall: Detach items from existing construction, prepare them for reuse, and reinstall them where indicated.

.5 Existing to Remain: Existing items of construction that are not removed and that are not otherwise indicated as being removed and salvaged, or removed and reinstalled.

.6 Hazardous Substances: Dangerous substances, dangerous goods, hazardous commodities and hazardous products may include asbestos, mercury and lead, PCB s, poisons, corrosive agents, flammable substances, radioactive substances, or other material that can endanger human health or wellbeing or environment if handled improperly as defined by Federal Hazardous Products Act (RSC 1985) including latest amendments.
1.5 ACTION AND INFORMATIONAL SUBMITTALS
.1 Action Submittals: Provide in accordance with Section 01 33 00– Submittal Procedures before starting work of this Section:

.2 Landfill Records: Indicate receipt and acceptance of selective demolition waste and hazardous wastes by a landfill facility licensed to accept hazardous wastes.
1.6 ADMINISTRATIVE REQUIREMENTS
.1 Coordination: Coordinate work of this Section to avoid interference with work by other Sections.

.2 Scheduling: 
.1 Account for Owner’s continued occupancy requirements during selective demolition with Section 02 41 19.16 - Selective Interior Demolition and schedule staged occupancy and worksite activities Owner.
1.7 QUALITY ASSURANCE
.1 Regulatory Requirements: Perform work of this Section in accordance with:
.1 Provincial/Territorial Workers’ Compensation Boards/Commissions.

.2 Provincial/Territorial Occupational Health and Safety Standards and Programs.
1.8 SITE CONDITIONS
.1 Condition of materials identified as being salvaged or demolished are based on their observed condition at time of site examination before tendering.
.2 Discovery of Hazardous Substances: 
.1 It is not expected that Hazardous Substances will be encountered in the Work. Immediately notify Owner if materials suspected of containing hazardous substances are encountered.

.3 Hazardous Substances: 
.1 Hazardous Substances are present in building to be selectively demolished. A report on the presence of Hazardous Substances is attached as an information document to this Specification for review and use. Examine report to become aware of locations where hazardous materials are present. Coordinate removal of hazardous materials as per appropriate sections of this specification.

1.9 SALVAGE AND DEBRIS MATERIALS
.1 Demolished items become Contractor’s property and will be removed from Project site; except for items indicated as being reused, salvaged, or otherwise indicated to remain the Owner’s property.
.2 Carefully remove materials and items designated for salvage and store in a manner to prevent damage or devaluation of.

.1 Leave main electrical distribution panel in place; panel can be used for temporary construction power for this and subsequent contracts in accordance with Section 01 51 00 – Temporary Utilities ; coordinate temporary power connections with Owner.

.2 Leave main telephone terminal backboard in place; panel can be used for temporary construction telephone system for this and subsequent contracts in accordance with Section 01 51 00 – Temporary Utilities ; coordinate temporary telephone connections with Owner.
Part 2 Products 
2.1 MATERIALS
.1 General Patching and Repair Materials: Refer to Section 02 41 19.16 - Selective Interior Demolition for listing of patching and repair materials incidental to removal or demolition of components associated with work of this Section.

.2 Electrical Repair Materials: Use only new materials, CSA or ULC labelled as appropriate and matching components remaining after work associated with components identified for removal or demolition are completed.

.3 Fire stopping Repair Materials: Use fire stopping materials compatible with existing fire stopping systems where removal or demolition work affects rated assemblies, restore to match existing fire rated performance.
Part 3 Execution 

3.1 EXAMINATION
.1 Verification of Existing Conditions: 
.1 Visit site, thoroughly examine and become familiar with conditions that may affect the work of this Section before tendering the Bid.
.2 Owner will not consider claims for extras for work or materials necessary for proper execution and completion of the contract that could have been determined by a site visit.
3.2 PREPARATION
.1 Protection of Existing Systems to Remain: Protect systems and components indicated to remain in place during selective demolition operations and as follows:

.1 Prevent movement and install bracing to prevent settlement or damage of adjacent services and parts of existing buildings scheduled to remain.

.2 Notify Owner and cease operations where safety of buildings being demolished, adjacent structures or services appears to be endangered and await additional instructions before resuming demolition work specified in this Section.

.3 Prevent debris from blocking drainage inlets.

.4 Protect mechanical systems that will remain in operation.

.2 Protection of Building Occupants: Sequence demolition work so that interference with the use of the building by the Owner and users is minimized and as follows:

.1 Prevent debris from endangering safe access to and egress from occupied buildings.

.2 Notify Owner and cease operations where safety of occupants appears to be endangered and await additional instructions before resuming demolition work specified in this Section.
3.3 EXECUTION
.1 Coordinate requirements of this Section with information contained in Section 02 41 19.16 - Selective Interior Demolition and as follows:

.1 Disconnect electrical circuits and panel feeders; maintain electrical service and main distribution panel as is, ready for subsequent Work.

.2 Remove existing luminaires, electrical devices and equipment including associated conduits, boxes, wiring, and similar items unless specifically noted otherwise.

.3 Disconnect and remove existing fire alarm system including associated conduits, boxes, wiring, and similar items unless specifically noted otherwise.

.4 Disconnect and remove communication systems including associated conduits, boxes, cabling, and similar items unless specifically noted otherwise.

.5 Disconnect and remove telephone outlets, associated conduit, cabling and sub terminal backboards and related accessories; maintain telephone service and main terminal backboard as is.

.6 Perform demolition work in a neat and workmanlike manner:

.1 Remove tools or equipment after completion of work, and leave site clean and ready for subsequent renovation work.

.2 Repair and restore damages caused as a result of work of this Section to match existing materials and finishes.

.7 Disconnect panel feeders back to main distribution panel and re label respective circuit breaker as “SPARE”.

.8 Place weatherproof blank cover plates on exterior outlet boxes remaining after demolition and removal activities.

.9 Remove existing conduits, boxes, cabling and wiring associated with removed luminaires, electrical devices and equipment.

.10 Grind off conduits and make flush with surface of concrete where conduits are cast into concrete; seal open ends of conduit with silicone sealant and leave in place.

.11 Seal open ends of conduit with silicone sealant and leave in place where they are inaccessible or cannot be removed without damaging adjacent construction.
3.4 CLOSEOUT ACTIVITIES
.1 Arrange for legal disposal and remove demolished materials to accredited provincial landfill site or alternative disposal site (recycle centre) except where explicitly noted otherwise for materials being salvaged for re use in new construction.
END OF SECTION

Ver. 10/22

