NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31  
Section 26 05 21 – Wire and Cables (0-1000V) 
Page 1 of 6

Part 1 General

1.1 Related Sections
.1 Section 26 05 20 - Wire and Box Connectors - 0 - 1000 V.
.2 Refer to drawings for wiring type required under different applications.
1.2 References
.1 Canadian Standards Association (CSA)
.1 CSA C22.2 No .0.3, Test Methods for Electrical Wires and Cables.

.2 CAN/CSA-C22.2 No. 131, Type TECK 90 Cable.

Part 2 Products
2.1 Building Wires
.1 Conductors: stranded for 10 AWG and larger. Minimum size: 12 AWG.
.2 Copper and ACM alloy conductors: size as indicated, with 600 V insulation of cross-linked thermosetting polyethylene material rated RW90 XLPE and RWU90 XLPE as indicated.
.1 Use RW90 XLPE or RWU90 XLPE in underground conduits.
.2 For direct buried underground cables, use RWU90 XLPE.
.3 RWU90 XLPE not required under interior floor slabs.
.3 Copper conductors: size as indicated, with thermoplastic insulation type TWH rated at 600 V, typically used for insulated ground wires.
.4 Type ACM conductors permitted for feeders above 60 amps.
2.2 TECK Cable
.1 Cable: to CAN/CSA-C22.2 No. 131.
.2 Conductors:
.1 Grounding conductor: copper. 
.2 Circuit conductors: copper and ACM alloy, size as indicated.
.3 Insulation:
.1 Cross-linked polyethylene XLPE, rating – 600 V.

.4 Inner jacket: polyvinyl chloride material.
.5 Armour: interlocking aluminum, compliant to applicable Building Code classification for this project. 

.6 Overall covering: thermoplastic polyvinyl chloride material.
.7 Fastenings:
.1 One hole steel straps to secure surface cables 50 mm and smaller. Two hole steel straps for cables larger than 50 mm.
.2 Channel type supports for two or more cables at 1500 mm centers.

.3 Threaded rods: 6 mm dia. to support suspended channels.

.8 Connectors:
.1 Watertight and/or type approved for TECK cable, as indicated.
2.3 Mineral-Insulated Cables
.1 Conductors: solid bare soft-annealed copper, size as indicated.
.2 Insulation: compressed powdered magnesium oxide to form compact homogeneous mass throughout entire length of cable.

.3 Overall covering: annealed seamless copper sheath, Type M1 rated 600 V, 250°C.
.4 Overall jacket: PVC applied over the sheath and compliant to applicable Building Code classification for this project for direct buried and wet locations, as indicated.
.5 Two hour fire rating.

.6 Connectors: watertight, field installed, approved for MI cable. 
.7 Termination kits: field installed approved for MI cable.
2.4 Armoured Cables
.1 Conductors: insulated, copper, size as indicated.
.2 Type: AC90.

.3 Armour: interlocking type fabricated from aluminum strip.

.4 Connectors: standard as required, complete with anti-short rings.  

2.5 Control Cables
.1 Type LVT: 2 soft annealed copper conductors, sized as indicated, with thermoplastic insulation, outer covering of thermoplastic jacket.
.2 Low energy 300 V control cable: stranded annealed copper conductors sized as indicated, with PVC insulation type TW -40° C polyethylene insulation with shielding of tape coated with paramagnetic material wire braid over each conductor and overall covering of PVC jacket.
2.6 Non-Metallic Sheathed Cable
.1 Non-metallic sheathed copper cable type: NMD90 nylon, size as indicated.
2.7 ACM Conductors

.1 Annealed, compacted aluminum alloy conductor material (ACM) for circuits 60 amps or more, single or multi-conductor, 600 volt insulation.

.2 Type: AC90, ACWU90 and TECK90.

.3 Armour: interlocked aluminum strip.

.4 Conductivity: 61% IACS to that of copper.

.5 Outer jacket: ACWU90 PVC jacket, FT-4 rated suitable for direct buried and Div. 1 and Div. 2 hazardous locations.
Part 3 Execution
3.1 Field Quality Control
.1 Perform tests in accordance with Section 26 05 00 - Common Work Results for Electrical.
.2 Perform tests using method appropriate to site conditions and to approval of Owner and local authority having jurisdiction over installation.
.3 Perform tests before energizing electrical system.
.4 No splices permitted in panel board feeders in new construction. Splices in re-work or renovation projects only with pre-approval by Owner. 
3.2 General Cable Installation
.1 Install cable in trenches in accordance with Section 33 71 73.02 - Underground Electrical Service.
.2 Lay cable in cable trays in accordance with Section 26 05 36 - Cable Trays for Electrical Systems.
.3 Terminate cables in accordance with Section 26 05 20 - Wire and Box Connectors - (0-1000 V).
.4 Cable Colour Coding: to Section 26 05 00 Common Work Results for Electrical.
.5 Conductor length for parallel feeders to be identical.
.6 Lace or clip groups of feeder cables at distribution centres, pull boxes, and termination points.
.7 Wiring in walls: typically drop or loop vertically from above to better facilitate future renovations.  Generally wiring from below and horizontal wiring in walls to be avoided unless indicated.
.8 Branch circuit wiring for surge suppression receptacles and permanently wired computer and electronic equipment to be 2-wire circuits only, i.e. common neutrals not permitted.
.9 Provide numbered wire collars for control wiring.  Numbers to correspond to control shop drawing legend.  Obtain wiring diagram for control wiring.
3.3 Installation of Building Wires
.1 Install wiring as follows:
.1 In conduit systems in accordance with Section 26 05 34- Conduits, Fastenings and Fittings.  
.2 In cable troughs in accordance with Section 26 05 33.01- Cable Trays for Electrical Systems. 

.3 In underground ducts in accordance with Section 26 05 43.01- Installation of Cables in Ducts. 

.4 In trenches in accordance with Section 26 05 43.01- Installation of Cables in Trenches.  

.5 In underfloor distribution system in accordance with Section 26 05 39- Underfloor Raceways for Electrical Systems 

.6 In cellular floor raceways in accordance with Section 26 05 38 – Cellular Metal Floor Raceway Fittings.   

.7 In surface and lighting fixture raceways in accordance with Section 26 50 00- Lighting.  

.8 In wireways and auxiliary gutters in accordance with Section 26 05 37 – Wireways and Auxiliary Gutters.   

.9 Overhead service conductors in accordance with Section 26 24 01 - Service Equipment.  

3.4 Installation of TECK Cable 0 -1000 V
.1 Install cables.
.1 Group cables wherever possible on channels.
.2 Install cable concealed, securely supported by straps and hangers.  
3.5 Installation of Mineral-Insulated Cables
.1 Run cable exposed, securely supported by straps.

.2 Support 2 h fire rated cables at 1m intervals.

.3 Make cable terminations by using factory-made kits.

.4 At cable terminations use thermoplastic sleeving over bare conductors.

.5 Where cables are buried in cast concrete or masonry, sleeve for entry and exit of cables.

.6 Do not splice cables.

3.6 Installation of Armoured Cables (AC-90)
.1 Group cables wherever possible.
.2 Use permitted only for work in movable partitions and vertical power supply drops to lighting fixtures.

.3 Ensure all cables are terminated and made safe prior to ceiling grid being installed. All lighting drops to be terminated safely, with approved connectors, within an approved box, complete with cover.
3.7 Installation of Control Cables
.1 Install control cables in conduit as indicated.
.2 Ground control cable shield.
3.8 Installation of Non-Metallic Sheathed Cable
.1 Install cables.
.2 Install straps and box connectors to cables as required.
.3 Use permitted in wood stud construction only.

3.9 INstallation of ACM Conductors

.1 Install ACM cables as per the latest edition of the Canadian Electrical Code and manufacturers installation requirements.

.2 Do not terminate ACM conductors with a copper bodied connector.

.3 Apply oxide coating on base cables as per electrical code requirements. 
END OF SECTION

Ver. 10/22

