NL Master Specification Guide

for Public Funded Buildings

Section 26 05 22 – Connectors and 
Re-Issued 2017/05/31
Terminations
Page 1 of 2

Part 1 General
1.1 INSTALLATION TOOLS              

.1 Include with the material one complete set of installation tools. Tools to include all hydraulic pumps, fittings, compression dyes, cutting tools, measuring devices necessary to install all components.
.2 Include AC-90 cable cutting tool (side cutters or back saws not permitted). 

Part 2 PRODUCTS

2.1 15KV TERMINATION KIT FOR 1/0MCM 15KV CABLE                

.1 Hydrophobic silicon body. 

.2  High-K stress control. 

.3 BIL rating 110 kV. 

.4 Compatible with size 1/0 AWG stranded copper 15 kV cable. 

.5 The exact kit selection will be based on the actual 1/0 AWG cable dimensions. 

2.2 15KV CONNECTOR LUGS      

.1 Suitable for use with a 1/0 AWG cable. 

.2 The exact lug selection will be based on the actual 1/0 AWG cable dimensions.       
2.3 TOOLS           

.1 One Thomas and Betts TBM5 installing tool. 

.2 For 3M terminations - two 3M CPK-A tool kits.
.3 AC-90 cutting tool. 
Part 3 execution

3.1 installation 
.1 Install terminations, and splices in accordance with manufacturer’s instructions.
.2 Bond and ground as required to CSA C22.2 No. 41. 
END OF SECTION

Ver. 10/22

