NL Master Specification Guide

for Public Funded Buildings
                                   Section 26 05 29 – Hangers and Supports
Issued 2008/03/18
 for Electrical Systems
Page 1 of 2

General (not applicable)
Products
1.1 SUPPORT CHANNELS
.1 U shape, size 41 x 41 mm, 2.5 mm thick, surface mounted suspended or set in poured concrete walls and ceilings as required.
Execution
1.2 INSTALLATION
.1 Secure equipment to hollow or solid masonry, tile and plaster surfaces with lead anchors or nylon shields.
.2 Secure equipment to poured concrete with expandable inserts.

.3 Secure equipment to hollow masonry walls or suspended ceilings with toggle bolts.
.4 Secure surface mounted equipment with twist clip fasteners to inverted T bar ceilings. Ensure that T bars are adequately supported to carry weight of equipment specified before installation.
.5 Support equipment, conduit or cables using clips, spring loaded bolts, cable clamps designed as accessories to basic channel members.

.6 Fasten exposed conduit or cables to building construction or support system using straps.

.1 One-hole steel straps to secure surface conduits and cables 50 mm and smaller.
.2 Two-hole steel straps for conduits and cables larger than 50 mm.

.3 Beam clamps to secure conduit to exposed steel work.
.4 Strap AC-90 cable at box location plus every 900 mm.
.7 Suspended support systems.
.1 Support individual cable or conduit runs with 6 mm dia threaded rods and spring clips.
.2 Support 2 or more cables or conduits on channels supported by 6 mm dia threaded rod hangers where direct fastening to building construction is impractical.

.8 For surface mounting of two or more conduits use channels at 1.5 m on centre spacing.
.9 Provide metal brackets, frames, hangers, clamps and related types of support structures where indicated or as required to support conduit and cable runs.

.10 Ensure adequate support for raceways and cables dropped vertically to equipment where there is no wall support.

.11 Do not use wire lashing, wood blocking, plastic strap or perforated strap to support or secure raceways or cables.

.12 Do not use supports or equipment installed for other trades for conduit or cable support except with permission of other trade and approval of Owner.  

.13 Install fastenings and supports as required for each type of equipment cables and conduits, and in accordance with manufacturer's installation recommendations.

END OF SECTION

Ver. 10/22

