NL Master Specification Guide

for Public Funded Buildings

Section 26 05 31 - Splitters, Junction, Pull 
Re-Issued 2021/05/31
Boxes and Cabinets
Page 1 of 2

Part 1 General
1.1 Realted Sections

.1 Section 01 33 00 – Submittal Procedures.

.2 Section 01 91 13.13 – Commissioning (Cx) Requirements.

.3 Section 26 05 00 – Common Work Results – Electrical.
1.2 SUBMITTALS
.1 Submit shop drawings and product data for cabinets.
.2 Provide manufacturer’s printed product literature, specifications and datasheet and include product characteristics, performance criteria, physical size, finish and limitations.

.3 Provide drawings stamped and signed by professional engineer registered or licensed in the Province of Newfoundland and Labrador, Canada.
Part 2 Products
2.1 Splitters
.1 Sheet metal enclosure, welded corners and formed hinged cover suitable for locking in closed position.
.2  Main and branch lugs to match required size and number of incoming and outgoing conductors as indicated.

.3 At least three spare terminals on each set of lugs in splitters less than 400 A.

2.2 Junction and Pull Boxes
.1 Welded steel construction with screw-on flat covers for surface mounting.
.2 Covers with 25 mm minimum extension all around, for flush-mounted pull and junction boxes.

2.3 Cabinets
.1 Type E: sheet steel, hinged door and return flange overlapping sides, handle, lock and catch, for surface mounting.
.2 Type T: sheet steel cabinet, with hinged door, latch, lock, 2 keys, containing 19 mm fir plywood backboard for surface flush mounting.

Part 3 Execution
3.1 Splitter Installation
.1 Install splitters and mount plumb, true and square to the building lines.
.2 Extend splitters full length of equipment arrangement except where indicated otherwise.

3.2 Junction, Pull Boxes and Cabinets Installation
.1 Install pull boxes in inconspicuous but accessible locations.
.2 Mount cabinets with top not higher than 2 m above finished floor.

.3 Install terminal block as indicated in Type T cabinets.

.4 Only main junction and pull boxes are indicated. Install pull boxes so as not to exceed 30 m of conduit run between pull boxes.
.5 Ensure all electrical boxes above drywall ceilings are accessible via a properly sized access door installed directly below the box in drywall ceilings. Temporary removal of electrical light fixtures are not considered safe access to above ceiling electrical boxes and shall not be permitted.
3.3 Identification
.1 Provide equipment identification in accordance with Section 26 05 00 – Common Work Results - Electrical.
.2 Install size 2 identification labels indicating system name voltage and phase.

END OF SECTION

Ver. 10/22

