NL Master Specification Guide

for Public Funded Buildings

Section 26 05 32 – Outlet Boxes, Conduit
Revised 2009/02/28
 Boxes and Fittings 
Page 1 of 3

Part 1 General
1.1 RELATED SECTIONS

.1 Section 26 05 00 – Common Work Results – Electrical.
.2 Section 26 05 29 – Hangers and Supports for Electrical Systems.
.3 Section 26 05 34 – Conduits, Conduit Fastenings and Fittings.
1.2 References
.1 Canadian Standards Association (CSA)
.1 CSA C22.1, Canadian Electrical Code, Part 1.

Part 2 Products
2.1 Outlet and Conduit Boxes General
.1 Size boxes in accordance with CSA C22.1. 
.2 102 mm square or larger outlet boxes as required for special devices.

.3 Gang boxes where wiring devices are grouped.

.4 Blank cover plates for boxes without wiring devices.

.5 347 V outlet boxes for 347 V switching devices.

.6 Combination boxes with barriers where outlets for more than one system are grouped.

2.2 galvanized Steel Outlet Boxes
.1 Electro-galvanized steel single and multi gang flush device boxes for flush installation, minimum size 76 x 50 x 38 mm or as indicated. 102 mm square outlet boxes when more than one conduit enters one side with extension and plaster rings as required.
.2 Electro-galvanized steel utility boxes for outlets connected to surface-mounted EMT conduit, minimum size 102 x 54 x 48 mm.
.3 102 mm square or octagonal outlet boxes for lighting fixture outlets.

.4 102 mm square outlet boxes with extension and plaster rings for flush mounting devices in finished plaster walls.

2.3 Masonry Boxes
.1 Electro-galvanized steel masonry single and multi gang boxes for devices flush mounted in exposed block walls.
2.4 Concrete Boxes
.1 Electro-glavanized sheet steel concrete type boxes for flush mount in concrete with matching extension and plaster rings as required.
2.5 Floor Boxes
.1 Concrete tight electro-galvanized sheet steel floor boxes with adjustable finishing rings to suit floor finish with brass faceplate. Device mounting plate to accommodate short or long ear duplex receptacles. Minimum depth: 28 mm for receptacles; 73 mm for communication equipment.
.2 Adjustable, watertight, concrete tight, cast floor boxes with openings drilled and tapped for 12 mm and 19 mm conduit. Minimum size: 73 mm deep.

2.6 Conduit Boxes
.1 Cast FS or FD aluminum boxes with factory-threaded hubs and mounting feet for surface wiring of switches and receptacle.
2.7 Outlet Boxes for Non-metallic Sheathed Cable
.1 Electro-galvanized, sectional, screw ganging steel boxes, minimum size 76 x 50 x 63 mm with two double clamps to take non-metallic sheathed cables. For use in wood stud construction only.
2.8 Fittings - General
.1 Bushing and connectors with nylon insulated throats.
.2 Knock-out fillers to prevent entry of debris.

.3 Conduit outlet bodies for conduit up to 32 mm and pull boxes for larger conduits.

.4 Double locknuts and insulated bushings on sheet metal boxes.
.5 Double split rings for AC-90 terminations.
2.9 Service Fittings
.1 'High tension' receptacle fitting made of 2 piece die-cast aluminum with brushed aluminum housing finish for 1 duplex receptacles. Bottom plate with two knockouts for centered or offset installation.
.2 Pedestal type 'low tension' fitting made of 2 piece die cast aluminum with brushed aluminum housing finish to accommodate two amphenol jack connectors.

Part 3 Execution
3.1 Installation
.1 Support boxes independently of connecting conduits.
.2 Fill boxes with paper, sponges or foam or similar approved material to prevent entry of debris during construction. Remove upon completion of work.

.3 For flush installations mount outlets flush with finished wall using plaster rings to permit wall finish to come within 6 mm of opening.
.4 Provide correct size of openings in boxes for conduit, mineral insulated and armoured cable connections. Reducing washers are not allowed.
.5 Vacuum clean interior of outlet boxes before installation of wiring devices.

.6 Identify systems for outlet boxes as required.
END OF SECTION 
Ver. 10/22

