NL Master Specification Guide

for Public Funded Buildings
Section26 05 33.01 – Surface and Lighting 
Revised 2009/02/28
Fixture Raceways
Page 1 of 3

Part 1 General
1.1 Related Sections
.1 Section 01 33 00 – Submittal Procedures.
1.2 References
.1 Canadian Standards Association (CSA)
.1 CAN/CSA-C22.2 No. 62, Surface Raceway Systems.
1.3 SUBMITTALS
.1 Indicate types of raceways with terminology similar to that used in this Section.
.2 Provide manufacturer’s printed product literature, specifications and datasheet and include product characteristics, performance criteria, physical size, finish and limitations.

.3 Manufacturer’s Instructions: submit manufacturer’s installation instructions and special handling criteria, installation sequence and cleaning procedures.
Part 2 Products
2.1 Surface Raceway System (wiring pulled in)
.1 Steel: to CSA C22.2 No. 62, one piece, free of sharp edges.
.2 Corners, pull boxes, elbows, tees, two piece assembly to facilitate site wiring.

.3 Finish: buff enamel.

.4 Necessary switch, receptacle, extension boxes, adapters and utility fittings required for complete installation.

2.2 Surface Raceway System (wiring laid in)

.1 Steel: to CSA C22.2 No. 62, two piece.
.1 Finish: buff enamel.
.2 Necessary switch, receptacle, extension boxes, adapters and utility fittings required for complete installation.
2.3 Surface Floor Raceway System
.1 Steel: to CSA C22.2 No. 62, two piece, manufactured as lay-in type raceway.
.2 Finish: buff enamel.

2.4 Channel Raceway
.1 Channel type raceway: to CSA C22.2 No. 62, steel, perforated.
2.5 Plastic Raceway

.1 Plastic raceway: to CSA C22.2 No. 62, rigid extruded polyvinyl chloride with slots on either side of raceway for exit of wiring.
.2 Channel: with solid snap-on cover throughout entire length.
2.6 Lighting Fixture Raceway
.1 Fluorescent fixture support system using channel type raceway with snap-on cover.
.2 Channel: minimum 1.6 mm thick.

.3 Clamp hangers with threaded rod. 
2.7 Fittings
.1 Elbows, tees, couplings and hanger fittings: to CSA C22.2 No. 62, manufactured as accessories to raceway supplied.
Part 3 Execution
3.1 Installation
.1 Install raceways before installation of wiring. Install covers for raceways and fittings after installation or wiring.
.2 Install supports, elbows, tees, connectors, fittings, bushings, adaptors as required.

.3 Keep number of elbows, offsets, connections to minimum.

.4 Use wiring with mechanical protection in channel raceways.

.5 Install barriers in raceways where different voltage systems are indicated.

END OF SECTION

Ver. 10/22

