NL Master Specification Guide

for Public Funded Buildings

Section 26 05 36 – Cable Trays for 
Revised 2009/02/28
Electrical Systems
Page 1 of 2

Part 1 General

1.1 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 26 05 00 – Common Work Results - Electrical.
1.2 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CAN/CSA C22.1 No. 126.1 – Metal Cable Tray Systems.
.2 National Electrical Manufacturers Association (NEMA). 
.1 NEMA FG 1, Fibreglass and Cable Tray Systems.
.2 NEMA VE 1, Metal Cable Tray Systems.

1.3 SUBMITTALS
.1 Product Data: submit manufacturer's product data sheets for cable tray indicating dimensions, materials, and finishes, including classifications and certifications.
.2 Shop Drawings: submit shop drawings showing materials, finish, dimensions, accessories, layout, and installation details.
.3 Identify types of cabletroughs used.
.4 Show actual cabletrough installation details and suspension system.
Part 2 Products
2.1 CABLETROUGH
.1 Cabletroughs and fittings: to NEMA FG 1 and VE 1 as referenced in Item 1.2.2 above..
.2  Ladder type, Class A, C1, D1 or E as indicated in CAN/CSA C22.2 No.126.

.3 Trays: extruded aluminum, width and depth as indicated.
.4 Fittings: horizontal elbows, end plates, drop outs, vertical risers and drops, tees, wyes, expansion joints and reducers where required, manufactured accessories for cabletrough supplied.

.1 Radii on fittings: 900 mm minimum.
.5 Solid covers for complete cabletrough system including fittings.
.6 Barriers where different voltage systems are in same cabletrough.

2.2 SUPPORTS
.1 Provide supports as indicated.
Part 3 Execution
3.1 INSTALLATION
.1 Install complete cabletrough system.
.2 Support cabletrough on both sides.

.3 Remove sharp burrs or projections to prevent damage to cables or injury to personnel.

3.2 CABLES IN CABLETROUGH
.1 Install cables individually.
.2 Lay cables into cabletrough. Use rollers when necessary to pull cables.

.3 Secure cables in cabletrough at 6 m centres, with nylon ties.

.4 Identify cables every 30 m with size 2 nameplates in accordance with Section 26 05 00 – Common Work Results - Electrical. 
END OF SECTION

Ver. 10/22

