NL Master Specification Guide

for Public Funded Buildings

Section 26 05 38 – Cellular Metal Floor
Re-issued 2017/05/31
 Raceway Fittings
Page 1 of 3

Part 1 General

1.1 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
1.2 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CSA C22.2 No.79, Cellular Metal and Concrete Floor Raceways and Fittings.
1.3 SUBMITTALS
.1 Submit layout of header duct in relation to:

.1 Cellular metal floor.
.2 Panels.

.3 Cabinets.

.2 Submit shop drawings for outlet fittings and accessories for use with cellular metal floor.
Part 2 Products
2.1 CELLULAR METAL FLOOR RACEWAYS
.1 Raceways: to CSA C22.2 No.79, zinc coated sheet steel, size as required, complete with joint covers and end closures.
2.2 TRENCH HEADER DUCTS
.1 Trench header: to CSA C22.2 No.79, zinc coated sheet steel, thickness as indicated, trench bottom 2.0 mm, partitions and sides 6.0 mm, fully gasketted to prevent ingress of dirt and water.
2.3 ENCLOSED HEADER DUCTS
.1 Enclosed header: to CSA C22.2 No.79, zinc coated sheet steel, thickness as indicated rectangular tubing 2.0 mm, with aluminum pans factory installed for terrazzo or wood floor finish. Use separate header duct runs for each distribution system.
2.4 ACCESSORIES AND FITTINGS
.1 Miscellaneous fittings: to CSA C22.2 No.79, factory fabricated tees, cross-boxes and covers, wall and floor elbows, risers, expansion joints, duct to cabinet connectors, duct straps, couplings, cell access units as required.
.2 High and low potential marker screws: brass to indicate centreline of cell.

.3 Cell taps for service fittings.

.4  100 mm dia duct to cell grommet with grounding screws.

.5 Abandoned outlet plates: brass. 
2.5 INSERTS
.1 Afterset inserts: 50 mm ips complete with cover cap as indicated.
2.6 CONNECTOR ASSEMBLIES
.1 Connector assemblies, consisting of adapters and nipples for connection of outlet fittings to afterset inserts.
2.7 IDENTIFICATION
.1 Mark duct sections before shipment for intended location to correlate with shop drawings.
Part 3 Execution
3.1 INSTALLATION
.1 Install cellular metal floor raceway fittings with duct levellers and other accessories required to make complete installation.
.2 Designate individual cells of cellular metal floor for ac power telephone intercommunication tv signal control systems and establish access into individual cells for various systems.

.3 Interconnect header duct with cellular metal floor using field cut access units grommeted and capped. For communication systems provide 65 mm diameter grommeted holes.

.4 Seal joints of header ducts prior to pouring of concrete floors.

.5 Install inserts 3.0 mm below finished concrete floor.

.6 Install marker screws on first outlet on either side of cross boxes, last outlet in the run and first outlet on either side of permanent partitions.

.7 Adjust marker screws so that heads show in cast-in-place surface of concrete floor.

.8 Clean out header ducts and conduits and leave system free of moisture.

.9 Slope ducts to drain.
END OF SECTION

Ver. 10/22

