NL Master Specification Guide

for Public Funded Buildings

Section 26 09 23.02 – Lighting Control 
Re-Issued 2021/05/31
Devices – Photoelectric
Page 1 of 2

Part 1 General

1.1 related sections

.1 Section 01 33 00 – Submittal Procedures.

.2 Section 01 78 00 – Closeout Procedures.

.3 Section 01 91 13.13 – Commissioning (Cx) Requirements. 

.4
Section 26 05 00 – Common Work Results - Electrical.

Part 2 Products
2.1 Photoelectric Lighting Control
.1 Wall mounting.
.2 Capable of switching 1800 W of lighting at 120 V.

.3 Voltage variation: plus or minus 10%.

.4 Temperature range: minus 40 °C to plus 40° C.

.5 Switching on lights at 1-5 lx.

.6 Switching off lights at 6-15 lx.

.7 Rated for 5000 operations.

.8 Options:

.1 Lightning arrester.
.2 Fail-safe circuit completed when relay de-energized.

.3 Twist-lock type receptacle.

.4 Terminal strip.

.5 Sensitivity adjustment.

.9 Switching time delay of 30 s.
.10 Wall mounting bracket.

.11 Colour coded leads: size 10 AWG, 460 mm long.

2.2 Contactor
.1  Cabinet mounting.
.2 Capable of switching multiple lamp circuits with total lighting load of 6000 W.

.3 Waterproof enclosure.

.4 Manual override.

Part 3 Execution
3.1 Installation
.1 Install photoelectric controls in accordance with manufacturer's instructions.
3.2 FIELD QUALITY CONTROL

.1
Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 - Commissioning (Cx) Requirements.

.2
Actuate control unit in presence of Owner to demonstrate lighting circuits are controlled as designated. 

END OF SECTION

Ver. 10/22

