NL Master Specification Guide

for Public Funded Buildings

Section 26 09 24 – Lighting Control Devices 
Re-Issued 2021/05/31

         – Low Voltage
 Page 1 of 4

Part 1 General

1.1 Related Sections
.1 Section 01 33 00 – Submittal Procedures.
.2 Section 01 35 29.06 – Health and Safety Requirements.
.3 Section 01 61 00 – Common Product Requirements.
.4 Section 01 78 00 – Closeout Procedures.
.5 Section 01 91 13.13 – Commissioning (Cx) Requirements. 
.6 Section 26 05 00 – Common Work Results - Electrical.
1.2 System Description

.1 Low voltage control system designed to provide remote switching of lighting loads by use of:
.1 Low voltage momentary contact switches
.2 Low voltage relays.

.3 Control transformers

.4 Low voltage rectifiers

.5 Manual switch control.

1.3 SUBMITTALS
.1 Product Data:
.1 Submit manufacturer's printed product literature, specifications and datasheet. Include product characteristics, performance criteria, and limitations.
.1 Submit two copies of Workplace Hazardous Materials Information System (WHMIS) Safety Data Sheets (SDS).
.2 Shop Drawings:
.1 Submit drawings stamped and signed by professional engineer registered or licensed in Province of Newfoundland and Labrador, Canada.
.3 Closeout Submittals:
.1 Submit maintenance data in accordance with Section 01 78 00 ‑ Closeout Submittals.
.4 Test reports:
.1 Submit certified test reports indicating compliance with specifications for specified performance characteristics and physical properties.
.2 Certificates: submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.
.3 Manufacturer's Instructions: submit manufacturer's installation instructions.
.4 Manufacturer's Field Reports: manufacturer's field reports specified.
1.4 QUALITY ASSURANCE
.1 Do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.
1.5 DELIVERY, STORAGE, AND HANDLING
.1 Packing, shipping, handling and unloading:
.1 Deliver, store and handle in accordance with Section 01 61 00 - Common Product Requirements.

.2 Deliver, store and handle materials in accordance with manufacturer's written instructions.
Part 2 Products
2.1 Materials
.1 Control system: by one manufacturer and assembled from compatible components.
2.2 Remote Control Switches
.1 Single pole, double throw, momentary contact, heavy duty, rated 3 A, 25 V, centre pivot rocker action with pilot lights where indicated.
2.3 Low Voltage Relays

.1 Electrically operated by momentary impulse, mechanically latched until activated.
.2 Two coil solenoid type with one coil to close relay contacts and one coil to open relay contacts.

.3 Operating voltage: 24 V, AC.

.4 Load contacts: 20 A, 120 or 347 V, AC as indicated.

.5 Auxiliary contacts for pilot light.

.6 Coloured pre-stripped leads.

2.4 Control Transformer

.1 Low voltage power Class 2, input 120 or 347 V, AC, 60 Hz, output 35 VA at 24 V.
2.5 Rectifier

.1 Selenium type: 24 V, AC, 60 Hz input, 0.36 A continuous duty output.
.2 Silicon type: 24 V, AC, 60 Hz input, 7.5 A continuous duty output.

2.6 Manual Control

.1 Individual remote control switches as indicated.
.2 Eight circuit manual master selector switch mounted in 100 mm square box with:

.1 Master lock-out switch
.2 Individual red jewelled pilot lights.

.3 Nine circuit manual dial-type master selector.
.4 Twelve circuit manual dial-type master selector.

2.7 Motor Operated Master Control

.1 Motor-driven multiple contact momentary switching device.
.2 Radial contact arm to rotate through one revolution in 17 s.

.3 Contact made in succession between 25 points around circle.

.4 One master required for "ON" operation and one for "OFF" operation.

.5 Motor master units connected in cascade to control circuits as indicated.

.6 Interface equipment as required to convert maintained contact signals to momentary contact control pulses.

Part 3 Execution
3.1 Installation

.1 Locate and install equipment in accordance with manufacturer's recommendations and as indicated.
3.2 FIELD QUALITY CONTROL 
.1 Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.
.2 Actuate control units in presence of Owner to demonstrate lighting circuits are controlled as designated.

END OF SECTION

Ver. 10/22

