NL Master Specification Guide

for Public Funded Buildings

Section 26 12 16.01 – Dry Type Transformers
Re-Issued 2022/10/11
 Up to 600 V Primary 
Page 1 of 8

Part 1 General
1.1 RELATED DOCUMENTS

.1 Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
1.2 SECTION INCLUDES
.1 Materials and components for dry type transformers up to 600 V primary, equipment identification and transformer installation.
.2 This Section includes the following types of dry-type transformers rated 600 V and less, with capacities up to 1000 kVA:
.1 Distribution transformers.

1.3 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 91 13.13 – Commissioning (Cx) Requirements.
.3 Section 26 05 00 – Common Work Results - Electrical.
1.4 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CAN/CSA-C22.2 No.47, Air-Cooled Transformers (Dry Type).
.2 CSA C9, Dry-Type Transformers.

.2 National Electrical Manufacturers Association (NEMA).
.3 CSA C22.1, Canadian Electrical Code.
1.5 SUBMITTALS

.1 Product Data for each type and size of transformer indicated.

.1 Physical: Include rated nameplate data, capacities, weights, dimensions, minimum clearances, installed devices and features.

.2 Product warranty.

.3 Details of contributions to LEED, including Energy & Atmosphere credits.

.1 Provide proposed energy savings in Annual kWh and Peak Demand kW compared to a NEMA TP-1 efficiency baseline for the transformers on the project.

.4 Efficiency Data

.1 Submit test data illustrating compliance with the energy efficiency requirements of NRCan 2019.
.2 Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

.1 Wiring Diagrams: Power, signal, and control wiring.

.3 Qualification Data: For testing agency.

.4 Source quality-control test reports.

.5 Field quality-control test reports.

.6 Operation and Maintenance Data:  For transformers to include in emergency, operation, and maintenance manuals.

1.6 QUALITY ASSURANCE

.1 Testing Agency Qualifications:  An independent agency, with the experience and capability to conduct the testing indicated, that is a member company of the InterNational Electrical Testing Association or is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7.
.1 Testing Agency’s Field Supervisor: Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Part 3.

.2 Testing Agency Qualifications: An independent agency, with the experience and capability to conduct the testing indicated, that is a nationally recognized testing laboratory (NRTL) as defined by OSHA in 29 CFR 1910.7.

.3 Source Limitations: Obtain each transformer type through one source from a single manufacturer.

.4 Electrical Components, Devices and Accessories: Listed and labelled as defined in NFPA 70, Article 100, and to Canadian Electrical Code (CEC), by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

.5 Comply with IEEE C57.12.91, “Test Code for Dry-Type Distribution and Power Transformers.”

.6 Comply with IEEE C57.110-1998-IEEE recommended practise for establishing transformer capability when feeding non-sinusoidal load currents.
1.7 DELIVERY, STORAGE, AND HANDLING

.1 Temporary Heating: Apply temporary heat according to manufacturer’s written instructions within the enclosure of each ventilated-type unit, throughout periods during which equipment is not energized and when transformer is not in a space that is continuously under normal control of temperature and humidity.

1.8 COORDInaTION

.1 Coordinate size and location of concrete bases with actual transformer provided.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and form work requirements are specified in Division 03.

.2 Coordinate installation of wall-mounting and structure-hanging supports with actual transformer provided.

Part 2 PRODUCTS

2.1 general transformer requirements

.1 Description: Factory-assembled and tested, air-cooled units for 60 Hz service

.2 Cores: Grain-oriented, non-aging silicon steel.

.3 Coils: Continuous windings without splices except for taps.

.1 Internal Coil Connections: Brazed or pressure type.

.2 Coil Material: Copper.

2.2 DISTRIBUTION TRANSFORMERS
.1 Provide a 25-year pro-rated product Warranty.

.2 Comply with NEMA ST 20, and list and label as complying with UL 1561.

.3 Cores: One leg per phase.

.4 Enclosure: Ventilated, NEMA 250, Type 2.

.1 Core and coil shall be impregnated within resin compound, sealing out moisture and air.
.5 Transformer Enclosure Finish: Comply with NEMA 250.

.1 Finish Color: Manufacturer’s Standard.

.6 Taps for Transformers smaller than 3 kVA: None.

.7 Taps for Transformers 7.5 to 24 kVA: One 5 percent tap above and one 5 percent tap below normal full capacity.

.8 Taps for Transformers 25 kVA and larger: Two 2.5 percent taps above and four 2.0 percent taps below normal full capacity.
.9 Insulation Class:  220 deg C, UL-component-recognized insulation system with a maximum of 130 deg C rise above 40 deg C ambient temperature.
.10 Energy Efficiency for Transformers Rated 15 kVA and larger:

.1 Comply with NRCan 2019– Dry-Type Transformers – Energy Efficiency Regulations.
.11 K-Factor Rating: Transformers shall be K-Factor 7 or higher rated and comply with UL 1561 requirements for non-sinusoidal load current-handling capability to the degree defined by designated K-factor.
.1 Unit shall not overheat when carrying full-load current with harmonic distortion corresponding to designated K-factor.

.2 Indicate value of K-factor on transformer nameplate.

.12 Electrostatic Shielding: Each winding shall have an independent, single, full-width copper electrostatic shield arranged to minimize inter-winding capacitance.

.1 Arrange coil leads and terminal strips to minimize capacitive coupling between input and output terminals.

.2 Include special terminal for grounding the shield.

.3 Shield Effectiveness:

.1 Capacitance between Primary and Secondary Windings: Not to exceed 33 picofarads over a frequency range of 20 Hz to 1 MHz.

.2 Common-Mode Noise Attenuation: Minimum of minus 120 dB at 0.5 to 1.5 kHz; minimum of minus 65 dB at 1.5 to 100 kHz.
.3 Normal-Mode Noise Attenuation: Minimum of minus 52 dB at 1.5 to 10 kHz.

.13 Wall Brackets: Manufacturer’s standard brackets.

.14 Fungus Proofing: Permanent fungicidal treatment for coil and core.

.15 Low-Sound-Level Requirements: NEMA ST 20 standard sound levels when factory tested according to IEEE C57.12.91.

2.3 options to address NFPA 70E/CSA-Z462 ARC Flash standard

.1 Integrated External Measurement Port

.1 Include external ports with 600V safety class twistlock connectors for quick and safe access to transformer primary and secondary voltages and currents with revenue 0.3 class accuracy.  Accurate and dynamic temperature data shall be provided via thermistors located in each leg of the transformer.

.2 Integrated Power/Energy/Power Quality Meter

.1 Basis of design: Equivalent or superior to Powersmiths SMART-3B.

.2 Meter shall be factory-installed on the transformer, connected to the transformer secondary, complete with fused voltage connections, revenue class 0.3 CTs individually characterized to 0.1% and CT shunting block.

.3 Provide local display of real time energy and power quality information as it related to the load fed from the transformer.

.4 Parameters measured include: V, I, THD (V, I), PF, Hz, kW, kVA, kVAR, kWh, Ad, KWd, kVAd, kVARd.

.5 Remote communications: Modbus TCP over Ethernet using built-in software for access via a standard web browser.

.6 Education for Sustainability System Ready.  Ensure that the integrated power meter specified above shall come complete with the necessary built-in connectivity including Ethernet/Modbus TCP and external IP capability to support a web-based building benchmarking and education for sustainability system that graphically illustrates the performance of the building relative to environmental and energy strategies including LEED.  Refer to Section 27 54 01.
.3 Integrated Infrared Inspection Window

.1 Allows Safe External Thermal Imaging of Fully Energized Electrical Components without removing the transformer cover.

.2 IP65/NEMA 4 rated both open and closed.
.4 Lockable Hinged Front Access Doors

.1 Allows safe and rapid access to the transformer without the need to undo multiple screws and handle heavy metal cover plates that are in close proximity to live electrical points.

.2 Doors shall be able to be secured using a padlock.
2.4 IDENTIFICATION DEVICES

.1 Nameplates: Engraved, laminated-plastic or metal nameplate for each distribution transformer, mounted with corrosion-resistant screws.  Name-plated label products are specified in Division 26 Section “Identification for Electrical Systems”.

2.5 SOURCE QUALITY CONTROL

.1 Test and inspect transformers according to IEEE C57.12.91.

.2 Factory Sound-Level Tests: Conduct sound-level tests on equipment for this Project.

.3 Test transformers for losses and efficiency as per Department of Energy 10 CFR Appendix A to Subpart K of Part 431 – Uniform Test Method for Measuring the Energy Consumption of Distribution Transformers and confirm compliance with NRCan 2019– Dry-Type Transformers – Energy Efficiency Regulations.
Part 3 EXECUTION
3.1 eXAMINATION

.1 Examine conditions for compliance with enclosure and ambient temperature requirements for each transformer.

.2 Verify that field measurements are as needed to maintain working clearances required by CSA C22.1 – Canadian Electrical Code and manufacturer’s written instructions.

.3 Examine walls, floors, roofs, and concrete bases for suitable mounting conditions where transformers will be installed.
.4 Verify that ground connections are in place and requirements in Division 26 Section “Grounding and Bonding for Electrical System’s have been met.  Maximum ground resistance shall be 5 ohms at location of transformer.

.5 Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION
.1 Install wall-mounting transformers level and plumb with wall brackets fabricated by transformer manufacturer.

.1 Brace wall-mounting transformers as specified in Division 26 Section “Vibration and seismic Controls for Electrical Systems”.

.2 Construct concrete bases and anchor floor-mounting transformers according to manufacturer’s written instructions, seismic codes applicable to Project, and requirements in Division 26 Section “Vibration and Seismic Controls for Electrical Systems”.

.3 Mount metering package on transformer enclosure.

3.3 CONNECTIONS

.1 Ground equipment according to Division 26 Section “Grounding and Bonding for Electrical Systems”.

.2 Connect wiring according to Division 26 Section “Low-Voltage Electrical Power Conductors and Cables”.

3.4 FIELD QUALITY CONTROL

.1 Perform tests and inspections and prepare test reports.

.1 Manufacturer’s Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

.2 Tests and Inspections:

.1 Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

.2 Test transformers for losses and efficiency as per Department of Energy 10 CFR Appendix A to Subpart K of Part 431 – Uniform Test Method for Measuring the Energy Consumption of Distribution Transformers. Verify results are consistent with the loss data provided on the submittal documenting compliance with NRCan 2019 – Dry-Type Transformers – Energy Efficiency Regulations.

.3 Remove and replace units that do not pass tests or inspections and retest as specified above.

.4 Infrared Scanning: Two months after Substantial Completion, perform an infrared scan of transformer connections.
.1 Use an infrared-scanning device designed to measure temperature or detect significant deviations from normal values.  Provide documentation of device calibration.

.2 Perform 2 follow-up infrared scans of transformers, one at 4 months and the other at 11 months after Substantial Completion.

.3 Prepare a certified report identifying transformer checked and describing results of scanning.  Include notation of deficiencies detected, remedial action taken, and scanning observations after remedial action.

.5 Test Labelling:  On completion of satisfactory testing of each unit, attach a dated and signed “Satisfactory Test” label to tested component.

3.5 ADJUSTING
.1 Record transformer secondary voltage at each unit for at least 48 hours of typical occupancy period.  Adjust transformer taps to provide optimum voltage conditions at secondary terminals.  Optimum is defined as not exceeding name plate voltage plus 10 percent and not being lower than name plate voltage minus 3 percent at maximum load conditions.  Submit recording and tap settings as test results.
.2 Connect buck-boost transformers to provide name plate voltage of equipment being served, plus or minus 5 percent, at secondary terminals.

.3 Output Settings Report: Prepare a written report recording output voltages and tap settings.

3.6 cleaning

.1 Vacuum dirt and debris; do not use compressed air to assist in cleaning.

END OF SECTION
Ver. 10/22

