NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2020/08/28
Section 26 13 01 – Isolating Switches to 15 KV
Page 1 of 2

Part 1 General

1.1 SECTION INCLUDES

.1 Materials for indoor and outdoor isolating switches.
.2 Edit this section to suit project requirements.

1.2 RELATED SECTIONS

.1 Section 01 33 00 ‑ Submittal Procedures.
.2 Section 01 78 00 - Closeout Submittals.
1.3 REFERENCES
.1 Canadian Standards Association (CSA International)
.1 CSA C22.2 No. 58, High‑Voltage Isolating Switches.
.2 National Electrical Manufacturers Association (NEMA)
1.4 CLOSEOUT SUBMITTALS

.1 Provide operation and maintenance data for isolating switches for incorporation into manual specified in Section 01 78 00 ‑ Closeout Submittals.
.2 Technical data to cover operating mechanism of group operated switches.

Part 2 Products

2.1 ISOLATING SWITCH

.1 Isolating switch: to CSA C22.2 No.58.
.2 Outdoor, single pole, vertical or horizontal load break with arcing horns, structure mounted, continuous current and voltage rating as indicated, manual operating mechanism, key interlocked.

.3 Outdoor, single pole, single throw hook operated disconnect, structure mounted, continuous rating as indicated on drawings.

.4 Outdoor, three pole, vertical or horizontal load break with arcing horns, group operated, structure mounted, continuous rating as indicated, manual operating or motor driven mechanism, key interlocked, as indicated.
.5 Indoor, three pole, vertical breaks, group operated, cubicle mounted, continuous rating as indicated, manual operating mechanism, key interlocked.

.6 Outdoor, single pole, quick break, hook stick operated enclosed disconnect with porcelain housing and glass‑reinforced polyester door, structure mounted, continuous rating as indicated.

.7 Outdoor, single pole, hook stick operated line switch with flanged steel channel base, distribution post type insulators, locking latch to prevent opening from vibration, structure mounted, continuous rating as indicated on drawings.

.8 Outdoor single pole, hook stick operated station switch with universal base designed for variety of mounting positions, NEMA TRN insulators, locking latch to prevent opening from vibration, continuous rating as indicated.

Part 3 Execution

3.1 INSTALLATION

.1 As indicated.
END OF SECTION

Ver. 10/22

