NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 24 02 – Service Entrance Board
Page 1 of 5

Part 1 General

1.1 SECTION INCLUDES
.1 Materials and installation for service entrance board.

1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.

.2 Section 01 78 00 - Closeout Submittals.
.3 Section 01 91 13.13 – Commissioning (Cx) Requirements.
.4 Section 26 05 00 – Common Work Results - Electrical.
1.3 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CAN/CSA-C22.2 No.31, Switchgear Assemblies.

1.4 SUBMITTALS
.1 Indicate on shop drawings.

.1 Floor anchoring method and foundation template.  
.2 Dimensioned cable entry and exit locations.

.3 Dimensioned position and size of bus.

.4 Overall length, height and depth.

.5 Dimensioned layout of internal and front panel mounted components.

.2 Include time-current characteristic curves for circuit breakers and fuses.

1.5 QUALITY ASSURANCE
.1 Submit 3 copies of certified test results.

1.6 CLOSEOUT SUBMITTALS
.1 Provide maintenance data for service entrance board for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.  

.2 Submit 3 copies maintenance data for complete assembly including components.

Part 2 Products
2.1 SERVICE ENTRANCE BOARD
.1 Service Entrance Board: to CAN/CSA-C22.2 No.31.

.2 Rating: 600 V, 3 phase, 4 wire, 800 A, short circuit current 18 kA (rms symmetrical) and/or as indicated on electrical drawings. (Edit voltage and current rating to suit project requirement). Cubicles: wall-mounted, or free standing, dead front, size as indicated.

.3 Barrier metering section from adjoining sections.

.4 Provision for installation of power supply authority metering in barriered section.

.5  Owners metering with all required CT’s and PT’s.
.6 Distribution section.

.7  Hinged access panels with captive knurled thumb screws.

.8 Bus bars and main connections:  tin plated aluminum.
.9 Bus from load terminals of main breaker or disconnect switch via metering section to main lugs of distribution section.

.10 Bus from load terminals of main breaker or disconnect switch to metering section and from metering section to lugs of distribution section.

.11 Identify phases with colour coding.

2.2 MOULDED CASE CIRCUIT BREAKERS
.1 Refer to Section 26 28 16.02 – Moulded Case Circuit Breakers. 
2.3 FUSIBLE DISCONNECTS AND FUSES
.1  Refer to Section 26 28 23 – Disconnect Switches – Fused and Non-fused. 
2.4 GROUNDING
.1 Copper ground bus extending full width of cubicles and located at bottom.

.2 Lugs at each end for size 3/0 grounding cable.

2.5 GROUND FAULT UNIT
.1  Refer to Section 26 28 18 – Ground Fault Equipment Protection. 
2.6 POWER SUPPLY AUTHORITY METERING
.1 Separate compartment and metal raceway for exclusive use of power supply authority metering.

.2 Provide mounting accessories and wiring for metering as follows and as indicated: 
.1 3 potential transformers.
.2 3 current transformers.

.3 Demand meter with kWH register as required. 
.3 Coordinate supply and installation of current and potential transformers for utility metering with utility representative.  Carry all associated costs. 
2.7 Owners Metering

.1 Digital unit with capability to display:

.1 Phase currents

.2 Voltage, L-L, L-N for each phase.

.3 System and per-phase power including watts, vars and VA.

.4 System energy including watthours, varhours and VA hours.

.5 System demand including watt demand, VA demand and var demand.

.6 Apparent and displacement power factor.

.7 Frequency.

.8 Recorded minimums and maximums of most parameters.

.2 Other features:

.1 Operator programmed using the face plate keypad or via communications.

.2 4 line x 20 character back lit LCD display.

.3 All monitored parameters are available at the faceplate.  True rms metering of distorted currents and voltages up to the 31st harmonic.
.4 CSA listed under CSA C22.2 #1010.1.

.5 KYZ pulse output to transfer demand signal to building energy management system.

.6 Current and potential transformers as required.

.3 Install metering units at “eye level” so that elevating devices are not required to read and use the meter. 

2.8 Transient voltage Surge Suppression (TVSS)
.1 Refer to Section 26 24 05 – Service Entrance TVSS Protection 
2.9 LIGHTNING ARRESTERS

.1 Refer to Section 26 41 00.02 – Secondary Lightning Arresters.
2.10 FINISHES

.1 Apply finishes in accordance with Section 26 05 00 – Common Work Results -Electrical. 
.1 Service entrance board exterior: gray. 
2.11 EQUIPMENT IDENTIFICATION
.1 Provide equipment identification in accordance with Section 26 05 00 – Common Work Results - Electrical. 
.2 Nameplates:

.1 White plate, black letters, size 7. 
.2 Complete board labelled: 120/208 or 347/600 V, 3 phase, 4 wire Amps as indicated.
.3 Main disconnect labelled: "Main Breaker or Switch".

.4 Branch disconnects labelled: as indicated.
Part 3 Execution
3.1 INSTALLATION
.1 Locate service entrance board and fasten to wall or floor as indicated.
.2 Coordinate the supply and installation of current and potential transformers for utility metering with utility representative. 
.3 Connect main secondary service to line terminals of main breaker or disconnect switch. 

.4 Connect load terminals of distribution breaker's or switches to feeders.

.5 Run one grounding conductor 3/0 AWG bare copper in 25 mm conduit from ground bus to building ground.  
3.2 field QUALITY CONTROL 

.1 Perform tests in accordance Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.
.2 Check factory made connections for mechanical security and electrical continuity.

.3 Check trip unit settings and fuse sizes against co-ordination study to ensure proper working and protection of components.

.4 Check operation of transient voltage surge suppressor.

.5 Check operation of Owner’s metering.

END OF SECTION

Ver. 10/22

