NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 24 16.01 – Panelboards - Breaker Type
Page 1 of 3

Part 1 General

1.1 SECTION INCLUDES
.1 Materials and installation for standard and custom breaker type panelboards.
1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 91 13.13 – Commissioning (Cx) Requirements.
.3 Section 06 10 53 – Miscellaneous Rough Carpentry.

.4 Section 26 05 00 – Common Work Results - Electrical.

.5 Section 26 28 16.02 - Moulded Case Circuit Breakers.
1.3 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CSA C22.2 No.29, Panelboards and enclosed Panelboards.
1.4 SUBMITTALS
.1 Drawings to include electrical detail of panel, branch breaker type, quantity, ampacity and enclosure dimension.

Part 2 Products
2.1 PANELBOARDS
.1 Panelboards: to CSA C22.2 No.29 and product of one manufacturer.
.1 Install circuit breakers in panelboards before shipment.
.2 In addition to CSA requirements manufacturer's nameplate must show fault current that panel including breakers has been built to withstand.
.2 250 and 600 V panelboards: bus and breakers rated for 10,000 and 18,000 A (symmetrical) minimum interrupting capacity respectively or as indicated on electrical drawings. 
.3 Sequence phase bussing with odd numbered breakers on left and even on right, with each breaker identified by permanent number identification as to circuit number and phase.

.4 Panelboards: mains, number of circuits, and number and size of branch circuit breakers as indicated.

.5 Two keys for each panelboard and key panelboards alike.

.6 Tin plated aluminum bus with neutral of same ampere rating as mains.

.7 Mains: suitable for bolt-on breakers.

.8 Trim with concealed front bolts and hinges.

.9 Trim and door finish: baked grey enamel.

2.2 CUSTOM BUILT PANELBOARD ASSEMBLIES
.1  125 mm relay section on one or both sides of panels as indicated for installation of low voltage remote control switching components.
.2 Double stack panels as indicated.

.3 Contactors in mains as indicated.

.4 Feed through lugs as indicated.

2.3 BREAKERS
.1 Breakers: to Section 26 28 16.02 - Moulded Case Circuit Breakers.  
.2 Breakers with thermal and magnetic tripping in panelboards except as indicated otherwise.

.3 Main breaker: separately mounted on top or bottom of panel to suit cable entry. When mounted vertically, down position should open breaker.

.4 Lock-on devices for 10% of 15 to 30 A breakers installed as indicated. Turn over unused lock-on devices to Owner. 
.5 Lock-on devices for receptacles, fire alarm clock outlet, emergency, door supervisory, intercom, stairway, exit and night light circuits as indicated.

2.4 EQUIPMENT IDENTIFICATION
.1 Provide equipment identification in accordance with Section 26 05 00 – Common Work Results - Electrical.  
.2 Nameplate for each panelboard size 4 engraved as indicated. 

.3 Nameplate for each circuit in distribution panelboards size 2 engraved as indicated. 

.4 Complete circuit directory with typewritten legend showing location and load of each circuit.

Part 3 Execution
3.1 INSTALLATION
.1 Locate panelboards as indicated and mount securely, plumb, true and square, to adjoining surfaces.
.2 Install surface mounted panelboards on plywood backboards in accordance with Section 06 10 00 - Rough Carpentry.  Where practical, group panelboards on common backboard.

.3 Mount panelboards to height specified in Section 26 05 00 – Common Work Results - Electrical or as indicated.

.4 Connect loads to circuits.

.5 Connect neutral conductors to common neutral bus with respective neutral identified. 

END OF SECTION

Ver. 10/22

