NL Master Specification Guide

for Public Funded Buildings

Section 26 24 16.02 – Panelboards - Switch 
Re-Issued 2021/05/31
and Fuse Type
Page 1 of 3

Part 1 General

1.1 Related Sections  
.1 Section 01 91 13.13 – Commissioning (Cx) Requirements.

.2 Section 06 10 53 – Miscellaneous Rough Carpentry.
.3 Section 26 05 00 – Common Work Results - Electrical.

.4 Section 26 28 13.01 - Fuses - Low-Voltage.
1.2 REFERENCES

.1 Canadian Standards Association (CSA)

.1 CSA C22.2 No. 29, Panelboards and Enclosed Panelboards.
1.3 SUBMITTALS
.1 Drawings to include electrical detail and dimensions of panel, branch switch type, ampacity and quantity.

Part 2 Products
2.1 Plant Assembly
.1 Assemble panelboard interior before shipment. Ship fuses loose for on site installation.
.2 In addition to CSA requirements, manufacturer's nameplates must show fault current that panelboard has been built to withstand.

2.2 Construction Features
.1 Panelboards: product of one manufacturer.
.2 Sequence phase bussing with odd numbered sections on left and even on right, with each section identified by permanent number identification as to circuit number and phase.

.3 Panelboards with mains, number of circuits, and number and size of branch sections as indicated.

.4 Two keys for each panelboard and key panelboards alike.

.5  Tin plated aluminum bus with neutral of same ampere rating as mains.

.6 Suitable for bolt-on fusible sections.

.7 Trim and door finish: baked grey enamel.

.8 Fusible pull-outs or door-operated type switches not acceptable.

.9 Fuse clips: suitable for type of fuses specified for each unit.

.10 Fuses: to Section 26 28 13.01 - Fuses - Low Voltage, sizes as indicated.
2.3 Custom Built Panelboard Assemblies

.1 Double stack panels as indicated.
.2 Contactors in mains as indicated.

.3 Feed through lugs as indicated.

2.4 Equipment Identification
.1 Provide equipment identification in accordance with Section 26 05 00 – Common Work Results - Electrical.
.2 Nameplate for each panel size 4 engraved in indicated. 

.3 Nameplate for each circuit in distribution panels size 2 engraved "name of load" as indicated.

.4 Complete circuit directory with typewritten legend showing location and load of each circuit. Install circuit directory under plastic protective cover on front of panel.

Part 3 Execution
3.1 Installation General

.1 Locate panelboards as indicated and mount securely, plumb, and square, to adjoining surfaces.
.2 Install surface-mounted panelboards on plywood backboards. Where practical group panelboards on common backboard.

.3 Mount panels to height specified in Section 26 05 00 – Common Work Results - Electrical or as indicated.

.4 Connect loads to circuits.

.5 Connect neutral conductors to common neutral bus.

END OF SECTION

Ver. 10/22

