NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 24 19 – Motor Control Centres
Page 1 of 5

Part 1 General

1.1 Related Work
.1 Section 01 33 00 – Submittal Procedures.
.2 Section 01 91 13.13 – Commissioning (Cx) Requirements.

.3 Section 26 05 00 – Common Work Results - Electrical.
.4 Section 26 29 10 – Motor Starters to 600 V. 

1.2 References
.1 Canadian Standards Association (CSA)
.1 CAN/CSA-Q9000, Quality Management and Quality Assurance Standards - Guidelines for Selection and Use.
1.3 SUBMITTALS
.1 Submit WHMIS MSDS - Safety Data Sheets. WHMIS acceptable to Labour Canada, and Health and Welfare Canada. 

.2 Submit product data sheets for sills, busbars and compartments. Include product characteristics, physical size and finish.

.3 Manufacturer’s Instructions: Provide to indicate special handling criteria, installation sequence and cleaning procedures. 
.4 Indicate:

.1 Outline dimensions
.2 Configuration of identified compartments.

.3 Floor anchoring method and dimensioned foundation template.

.4 Cable entry and exit locations.

.5 Dimensioned position and size of busbars and details of provision for future extension.

.6 Schematic and wiring diagrams.

1.4 Closeout Submittals
.1 Provide operation and maintenance data for motor control centre for incorporation into manual specified in Section   01 78 00 - Closeout Submittals.
.2 Include data for each type and style of starter.

Part 2 Products
2.1 Supply Characteristics
.1  600 V, 60Hz, delta connected, 3 phase, 3 wire, grounded 
2.2 General Description
.1 Compartmentalized vertical sections with common power busbars.
.2 Floor mounting, free standing, enclosed dead front.

.3 Indoor CSA, 1 gasketted enclosure, front or back to back mounting as indicated.

.4  Class I Type A, Class I Type B, Class 1 Type C as required and indicated.
2.3 Vertical Section Construction

.1 Independent vertical sections fabricated from rolled flat steel sheets bolted together to form rigid, completely enclosed assembly.
.2 Each vertical section divided into compartment units, minimum 305 mm high, as indicated.

.3 Each unit to have complete top and bottom steel plate for isolation between units.

.4 Horizontal wireways, equipped with cable supports, across top and bottom, extending full width of motor control centre, isolated from busbars by steel barriers.

.5 Vertical wireways c/w doors for load and control conductors extending full height of vertical sections, and equipped with cable tie supports. Installation wiring to units accessible with doors open and units in place.

.6 Openings, with removable coverplates, in side of vertical sections for horizontal wiring between sections.

.7 Incoming cables or bus duct to enter at top or bottom with terminals as indicated.

.8 Provision for outgoing cables to exit via top or bottom with terminals.

.9 Removable lifting means.

.10 Provision for future extension of both ends of motor control centre including busbars without need for further drilling, cutting or preparation in field.

.11 Divide assembly for shipment to site, complete with hardware and instructions for re-assembly.

2.4 Sills

.1 Continuous 100 mm channel iron floor sills for mounting bases with 19 mm diameter holes for bolts.
2.5 Busbars

.1 Main horizontal and branch vertical, three phase high conductivity tin plated copper busbars in separate compartment, bare, self-cooled, extending entire width and height of motor control centre, supported on insulators and rated:
.1 Main horizontal busbars: 600 A or as indicated.
.2 Branch vertical busbars: 300 A or as indicated.

.2 Branch vertical busbars for distribution of power to units in vertical sections.
.3 No other cables, wires, equipment in main and branch busbar compartments.

.4 Brace buswork to withstand effects of short-circuit current of 22 kA rms symmetrical, or as indicated.
.5 Bus supports: with high dielectric strength, low moisture absorption, high impact material and long creepage surface designed to discourage collection of dust.

2.6 Ground Bus

.1 Copper ground bus extending entire width of motor control centre.
.2 Vertical ground bus strap, full height of section, tied to horizontal ground bus, engaged by plug-in unit ground stab.

2.7 Motor Starters and Devices
.1  Section 26 29 10 – Motor Starters to 600 V.
2.8 Starter Unit Compartments
.1 Units EEMAC size 5 and smaller, circuit breaker units 225A and smaller, plug-in type with self-disconnect. Guide rail supports for units to ensure that stabs make positive contact with vertical bus. Provision for units to be installed or removed, off load, while buses energized.
.2 Unit mounting:

.1 Engaged position - unit stabbed into vertical bus.
.2 Withdrawn position - unit isolated from vertical bus but supported by structure. Terminal block accessible for electrical testing of starter.

.3 Provision for positive latching in either engaged or withdrawn position and padlocking in withdrawn position.

.4 Stab-on connectors free floating tin plated clips, self-aligning, backed up with steel springs.

.3 External operating handle of circuit switch interlocked with door to prevent door opening with switch in "on" position. Provision for 3 padlocks to lock operating handle in "off" position and lock door closed.
.4 Hinge unit doors on same side.

.5 Overload relays manually reset from front with door closed.

.6 Pushbuttons and indicating lights mounted on door front.

.7 Devices and components by one manufacturer to facilitate maintenance.

.8 Pull-apart terminal blocks for power and control to allow removal of starter units without removal of field wiring.

2.9 Wiring Identification
.1 Provide wiring identification in accordance with Section 26 05 00 – Common Work Results - Electrical.
2.10 Equipment Identification

.1 Provide equipment identification in accordance with Section 26 05 00 – Common Work Results - Electrical.
.1 Motor control centre main nameplate: size No. 7, engraved as indicated.
.2 Individual compartment nameplates: size No. 5, engraved as indicated.

2.11 Finishes

.1 Apply finishes in accordance with Section 26 05 00 – Common Work Results - Electrical.
.2 Paint motor control centre exterior light gray and interiors white.

2.12 Source Quality Control
.1 Provide manufacturer's type test certificates including short circuit fault damage certification up to short circuit values specified under bus bracing.
.2 Provide Owner with certified copy of standard factory tests of complete motor control centre including operation of switches, circuit breakers, starters and controls.

.3 Manufacturer to provide proof of quality control program in accordance with CAN/CSA-Q9000.

Part 3 Execution
3.1 Installation
.1 Set and secure motor control centre in place on channel bases, rigid, plumb and square to building floor and wall.
.2 Make field power and control connections as indicated.
.3 Ensure correct overload heater elements are installed.

3.2 Field Quality Control
.1 Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.
.2 Ensure moving and working parts are lubricated where required.

.3 Operate starters in sequence to prove satisfactory performance of motor control centre every hour for an 8 hour period.

END OF SECTION

Ver. 10/22

