NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 27 26 – Wiring Devices
Page 1 of 4

Part 1 General

1.1 SECTION INCLUDES
.1 Switches, receptacles, wiring devices, cover plates and their installation.
1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 91 13.13 –Commissioning (Cx) Requirements. 
.3 Section 26 05 00 – Common Work Results - Electrical.
1.3 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CSA-C22.2 No.42, General Use Receptacles, Attachment Plugs and Similar Devices.
.2 CSA-C22.2 No.42.1, Cover Plates for Flush-Mounted Wiring Devices (Bi-national standard, with UL 514D).

.3 CSA-C22.2 No.55, Special Use Switches.

.4 CSA-C22.2 No.111, General-Use Snap Switches (Bi-national standard, with UL 20, twelfth edition).

Part 2 Products
2.1 SWITCHES
.1  15 A, 120 V, single pole, double pole, three-way, four-way switches as indicated to: CSA-C22.2 No.55 and CSA-C22.2 No.111.
.2 Manually-operated general purpose ac switches with following features:

.1 Terminal holes approved for No. 10 AWG wire.
.2 Silver alloy contacts.

.3 Urea or melamine moulding for parts subject to carbon tracking.

.4 Suitable for back and side wiring.

.5 White toggle.
.6 Specification grade.

.7 Hospital grade as indicated. 
.3  Toggle operated fully rated for tungsten filament and fluorescent lamps, and up to 80% of rated capacity of motor loads.
.4 Switches of one manufacturer throughout project.

2.2 RECEPTACLES
.1 Duplex receptacles, CSA type 5-15 R, 125 V, 15 A, U ground, to: CSA-C22.2 No.42 with following features:
.1 Ivory thermoplastic moulded housing.
.2 Suitable for No. 10 AWG for back and side wiring.

.3 Break-off links for use as split receptacles.

.4 Eight back wired entrances, four side wiring screws.

.5 Triple wipe contacts and rivetted grounding contacts.
.6 Specification grade.

.7 Hospital grade as indicated. 
.2 Single receptacles CSA type 5-15 R, 125 V, 15 A, U ground with following features:
.1 Ivory thermoplastic moulded housing.
.2 Suitable for No. 10 AWG for back and side wiring.

.3 Four back wired entrances, 2 side wiring screws.

.3 Other receptacles with ampacity and voltage as indicated.
.4 Receptacles of one manufacturer throughout project.

2.3 SPECIAL WIRING DEVICES
.1 Special wiring devices:
.1 Clock hanger outlets, 15 A, 125 V, 3 wire, grounding type, suitable for No. 10 AWG for installation in flush outlet box.
.2 Pilot lights as indicated, with neon type 0.04 W, 125 V lamp and red plastic jewel lense, flush type.

2.4 WIRING DEVICES FOR COMPUTER ROOMS
.1  As indicated. 
2.5 COVER PLATES
.1 Cover plates for wiring devices to: CSA-C22.2 No.42.1.
.2 Cover plates from one manufacturer throughout project.

.3 Sheet steel utility box cover for wiring devices installed in surface-mounted utility boxes.

.4  Nylon ivory or stainless steel cover plates as indicated, thickness 2.5 mm for wiring devices mounted in flush-mounted outlet box.

.5  Sheet metal cover plates for wiring devices mounted in surface-mounted FS or FD type conduit boxes.

.6 Weatherproof double lift spring-loaded cast aluminum cover plates, complete with gaskets for duplex receptacles as indicated.

.7 Weatherproof spring-loaded cast aluminum cover plates complete with gaskets for single receptacles or switches.
.8 All wiring device cover plates to be labeled using clear adhesive strips with black type identifying panel and circuit number for each device.
Part 3 Execution
3.1 INSTALLATION
.1 Switches:
.1 Install single throw switches with handle in "UP" position when switch closed.
.2 Install switches in gang type outlet box when more than one switch is required in one location.

.3 Mount toggle switches at height in accordance with Section 26 05 00 – Common Work Results - Electrical.  

.2 Receptacles:
.1 Install receptacles in gang type outlet box when more than one receptacle is required in one location.
.2 Mount receptacles at height in accordance with Section 26 05 00 – Common Work Results - Electrical.  

.3 Where split receptacle has one portion switched, mount vertically and switch upper portion.

.3 Cover plates:
.1 Protect cover plate finish with paper or plastic film until painting and other work is finished.
.2 Install suitable common cover plates where wiring devices are grouped.
.3 Do not use cover plates meant for flush outlet boxes on surface-mounted boxes.

END OF SECTION

Ver. 10/22

