NL Master Specification Guide

for Public Funded Buildings

Section 26 28 13.02 – Outdoor Load Break 
Issued 2008/03/18
Switches and Fuses
Page 1 of 4

Part 1 General

1.1 SECTION INCLUDES

.1 Materials and installation for outdoor load break switches and fuses.
1.2 RELATED SECTIONS

.1 Section 01 33 00 ‑ Submittal Procedures.
.2 Section 01 78 00 ‑ Closeout Submittals.

.3 Section 26 05 00 - Common Work Results - Electrical.

1.3 REFERENCES

.1 American National Standards Institute (ANSI)
.1 ANSI C37.46, Specifications for High Voltage Explosion and Current‑Limiting Type Power Class Fuses and Fuse Disconnecting Switches.

.2 Electrical and Electronic Manufacturers Association of Canada (EEMAC)
.1 EEMACG1‑1, Indoor and Outdoor Switch and Bus Insulators.

.3 National Electrical Manufacturers Association (NEMA)
.1 NEMA SG2, High‑Voltage Fuses.

1.4 SHOP DRAWINGS AND PRODUCT DATA

.1 Indicate:

.1 Load break mechanism.

.2 Switching type.

.3 Mounting design.

.4 Fuse holder mechanism.

.5 Gang operating mechanism.

.6 Load rating.

1.5 EXTRA MATERIALS

.1 Provide maintenance materials in accordance with Section 01 78 00 ‑ Closeout Submittals.
.2 Include: as recommended by manufacturer.

Part 2 Products

2.1 MATERIALS

.1 Fuses: to NEMA SG2 and ANSI C37.46.
.2 Insulators: to EEMAC G1‑1, as indicated.

2.2 LIGHT LOAD AIR BREAK SWITCHES

.1 Horizontal mounted, vertical break, rotating insulator, gang operated, single throw, 3 pole.
.2 Rating: 600A, 5, 15 kV, as indicated.

.1 Momentary rms asymmetrical A: 18,000 or as indicated.

.3 Insulators: post type.
.4 Universal mounting base for each pole designed for wood mounting, as indicated.

.5 Arc horns: galvanized steel to permit switch opening and closing under light load, magnetizing or charging currents.

.6 Bearings: silicone grease lubricated for life.

.7 Interphase mechanism assembly:

.1 Operated from center end.

.2 Outside poles connected to center pole through end yoke assemblies, pipe turnbuckles and universal ball and yoke assembly to permit switch operation with up to 15 degrees misalignment of pole bases.

.3 Bearings and moving joints on each pole and interphase mechanism positively sealed by silicone cord rings.

.8 Manual operating mechanism with:
.1 One offset bearing.

.2 Pipe shaft: length as indicated.

.3 Pipe guides.

.4 Pipe couplings.

.5 Position indicator.

.6 Foot bearing.

.7 Operating handle with padlock.

2.3 FULL LOAD AIR BREAK SWITCHES

.1 Horizontal, vertical or inverted mounted, as indicated, vertical break, gang operated, single throw, 3 pole, as indicated.
.2 Rating: 600 A, 5, 15 kV, as indicated.
.1 Momentary rms asymmetrical A: 18,000 or as indicated.

.3 Insulators: three per pole, standard station post type.
.4 Contacts:

.1 Silver‑nickel alloy spring loaded multi‑contact switch blade contacts.

.5 Interrupter unit to permit opening and closing under rated full load currents consists of:
.1 Mechanism actuated by levers for operating contacts.

.2 Bolted to fixed contact assembly of switch.

.3 Shunt contact bolted to switch blade actuates interrupter unit when blade is moved to open or closed position.

.6 Switch base: 5 mm formed channel galvanized steel drilled for universal mounting on wood pole.
.7 Interphase mechanism assembly.

.1 Operated from center pole.

.2 Poles interconnected by articulated pipe assembly to allow for minor misalignment.

.8 Manual operating mechanism with:
.1 Two offset bearings.

.2 Pipe shaft: length as indicated.

.3 Pipe guides.

.4 Pipe couplings.

.5 Position indicator.

.6 Foot bearing.

.7 Operating handle with padlock.

2.4 PRIMARY FUSES

.1 Disconnect vertical, 180 degrees opening type.
.2 Voltage rating: as indicated.

.3 Continuous current rating: 200, 300, 400 or 720 A, or as indicated.

.4 Three phase symmetrical short circuit ratings: 
.1 150 MVA at 4.16 kV.

.2 400 MVA at 13.8 kV.
.5 Refill unit consisting of:
.1 Fusible element: silver.
.2 Arcing rods: main rod copper, silver clad, auxilliary rod stainless steel.

.3 Solid material arc‑extinguishing medium contained in filament wound glass‑epoxy tube.

Part 3 Execution

3.1 INSTALLATION

.1 Install in accordance with manufacturer's instructions.
.2 Connect switch terminals to primary feeder and load feeder.
.3 Locate, mount and connect fuses.

3.2 FIELD QUALITY CONTROL

.1 Perform tests in accordance with Section 26 05 00 - Common Work Results - Electrical.
.2 Energize and load feeders controlled by load break switches.

.3 Open and close load break switches at least ten times over period of 8 hours to ensure proper mechanical and electrical performance of installation.

END OF SECTION

Ver. 10/22

