NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 28 16.02 – Moulded Case Circuit Breakers
Page 1 of 2

Part 1 General

1.1 Related Sections
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 91 13.13 - Commissioning (Cx) Requirements.

.3 Section 26 05 00 - Common Work Results – Electrical.
1.2 SUBMITTALS
.1 Include time-current characteristic curves for breakers with ampacity of 600 A and over or with interrupting capacity of 22,000 A symmetrical (rms) and over at system voltage.

Part 2 Products
2.1 Breakers General
.1 Bolt-on moulded case circuit breaker: quick- make, quick-break type, for manual and automatic operation with temperature compensation for 40°C ambient.
.2 Common-trip breakers: with single handle for multi-pole applications.

.3 Magnetic instantaneous trip elements in circuit breakers to operate only when value of current reaches setting. Trip settings on breakers with adjustable trips to range from 3-8 times current rating.

.4 Circuit breakers with interchangeable trips as indicated.

.5 Circuit breakers to have minimum of 10,000 A symmetrical rms interrupting capacity rating.

2.2 Thermal Magnetic Breakers Design A
.1 Moulded case circuit breaker to operate automatically by means of thermal and magnetic tripping devices to provide inverse time current tripping and instantaneous tripping for short circuit protection.
2.3 Fused Thermal Magnetic Breakers Design B
.1 Fused thermal magnetic breakers with current limiting fuses internally mounted. Time current limiting characteristics of fuses coordinated with time current tripping characteristics of circuit breaker. Coordination to result in interruption by breaker of fault-level currents up to interrupting capacity of breaker. Fuses individually removable and interlocked with breaker. Removal of fuse cover, blowing of a fuse or removal of a fuse, to trip breaker.
2.4 Solid State Trip Breakers Design C
.1 Moulded case circuit breaker to operate by means of a solid-state trip unit with associated current monitors and self-powered shunt trip to provide inverse time current trip under overload condition, and long time short time, instantaneous tripping for phase and ground fault short circuit protection.
2.5 Optional Features
.1 Include:
.1 shunt trip.
.2 auxiliary switch.

.3 motor-operated mechanism c/w time delay unit.

.4 under-voltage release.

.5 on-off locking device.

.6 handle mechanism.

2.6 Enclosure
.1  Mounted in NEMA 1 type enclosure, sprinkler proof as indicated.
Part 3 Execution
3.1 Installation
.1 Install circuit breakers as indicated.
END OF SECTION

Ver. 10/22

