NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 28 18 – Ground Fault Equipment Protection
Page 1 of 3

Part 1 General

1.1 SECTION INCLUDES
.1 Equipment, fabrication and installation for ground fault protection.
.2 Text to complete Section 26 23 00 - Low Voltage Switchgear. 

.3 Text to complete Section 26 24 02 - Service Entrance Board. 

1.2 RELATED SECTIONS
.1 Section 01 29 83 - Payment Procedures for Testing Laboratory Services.
.2 Section 01 33 00 - Submittal Procedures.

.3 Section 01 45 00 - Quality Control.
.4 Section 01 91 13.13 –Commissioning (Cx) Requirements.
.5 Section 26 05 00 – Common Work Results - Electrical.
1.3 PAYMENT PROCEDURES 
.1 Pay for field testing of ground fault equipment performed by equipment manufacturer.
1.4 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CAN/CSA-C22.2 No. 144, Ground Fault Circuit Interrupters.
.2 National Electrical Manufacturers Association (NEMA)
.1 NEMA PG 2.2, Application Guide for Ground Fault Protection Devices for Equipment.
1.5 SUBMITTALS
.1 Submit product data and shop drawings.

.2 Submit test report for field testing of ground fault equipment to Owner and a certificate that system as installed meets criteria specified.

Part 2 Products
2.1 EQUIPMENT
.1 Ground fault protective equipment: components of one manufacturer.
.2 Provide ground fault protection on 1000A, 600V, 4 wire, 3 phase service and 2000 A, 208V, 4 wire, 3 phase service and above:  to NEMA PG 2.2 and CAN/CSA-C22.2 No. 144. 

.3 Ground fault unit to contain:

.1 Ground sensing relay suitable for operation at 500 mA as indicated on electrical drawings.  Control voltage: 120 V.
.2 Ammeter with scale 0 to 5 A to indicate ground current value.
.3 Three position sensitivity control switch to select value of leakage current at which relay will operate.

.4 Indicating lamp illuminated when no ground fault exists, extinguished on ground fault or test.
.5 Switch:

.1 SPDT contacts for alarm and trip. 
.2 Mechanical target indication.

.3 Manually reset.

.6 Reset button for contacts and target.
.7 Suitable for panel mounting.

.4 Zero sequence transformer toroidal type with 300 - 3000 mA range.
.5 Neutral:

.1 Use an artificial neutral and grounding resistor.
.2 Use neutral ground resistor unit.
.6 System to operate instantaneously at ground current setting.
2.2 FABRICATION
.1 Install following components in equipment specified in other Sections and as indicated.
.1 Zero sequence transformer.
.2 Ground fault relay.

.3 Ground resistor unit.

2.3 RELATED EQUIPMENT
.1  Shunt trip breakers. Load break disconnect switch.
Part 3 Execution
3.1 INSTALLATION
.1 Do not ground neutral on load side of sensor.
.2 Install phase conductors including neutral through zero sequence transformer.

.3 Install ground fault protection system.

.4 Make connections as indicated and in accordance with manufacturer's recommendations.

3.2 FIELD QUALITY CONTROL
.1 Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements. 
.2 Arrange and pay for field testing of ground fault equipment by ground fault equipment manufacturer before commissioning service.
.3 Check trip unit settings to ensure proper working operation and protection of components.
.4 Demonstrate simulated ground fault tests.

END OF SECTION

Ver. 10/221

