NL Master Specification Guide

for Public Funded Buildings

Section 26 28 20 – Ground Fault Circuit 
Re-Issued 2021/05/31
Interrupters – Class “A”
Page 1 of 3

Part 1 General

1.1 SECTION INCLUDES
.1 Equipment and installation for ground fault circuit interrupters (GFCI).
1.2 RELATED SECTIONS
.1 Section 01 29 83 - Payment Procedures for Testing Laboratory Services.
.2 Section 01 33 00 - Submittal Procedures.

.3 Section 01 45 00 - Quality Control.
.4 Section 01 91 13.13 – Commissioning (Cx) Requirements.
.5 Section 26 05 00 – Common Work Results - Electrical.
1.3 PAYMENT PROCEDURES
.1 Pay for field testing of ground fault equipment performed by equipment manufacturer in accordance with Section 01 29 83 - Payment Procedures for Testing Laboratory Services.
1.4 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CAN/CSA-C22.2 No.144, Ground Fault Circuit Interrupters.
.2 National Electrical Manufacturers Association (NEMA)
.1 NEMA PG 2.2, Application Guide for Ground Fault Protection Devices for Equipment.
1.5 SUBMITTALS
.1 Submit product data and shop drawings.

.2 Submit test report for field testing of ground fault equipment to Owner and a certificate that system as installed meets criteria specified herein.

Part 2 Products
2.1 MATERIALS
.1 Equipment and components for ground fault circuit interrupters (GFCI): to CAN/CSA-C22.2 No.144.  
.2 Components comprising ground fault protective system to be of same manufacturer.

2.2 BREAKER TYPE GROUND FAULT INTERRUPTER
.1  Single or two pole ground fault circuit interrupter for 15-20 A, 120 V, 1 phase circuit c/w test and reset facilities.
2.3 GROUND FAULT LIFE PROTECTOR
.1  A, 2 pole circuit breaker to supply power to mains of 100A, 208 V, 3 phase panel and complete with:
.1 Automatic shunt trip breaker.
.2 Zero sequence current sensor.

.3 Facilities for testing and reset.

.4 CSA Enclosure 1, surface mounted.

.5 Ground fault trip indicator light.

2.4 GROUND FAULT PROTECTOR UNIT
.1 Self-contained with 15 A, 120 V circuit interrupter and duplex receptacle complete with:
.1 Solid state ground sensing device.
.2 Facility for testing and reset.

.3 CSA Enclosure 1, flush mounted with stainless steel face plate.

2.5 SYSTEM GROUND FAULT PROTECTION PANEL
.1 Self-contained panel suitable for120/208 V, 3 phase, 4 wire, grounded supply. Panel to have following features:
.1 Automatic 100 or 225 A breaker with shunt trip.
.2 Ground fault relay factory set at 10 mA with inverse time delay characteristics from pick-up 1 s to 0.025 s.

.3 Zero sequence current sensor.

.4 Provision for testing and reset.

.5 CSA Enclosure 1, surface mounted.

.6 Ground fault trip indicating light.
.7 Resistor type fused artificial neutral.

2.6 PUMP PROTECTION PANEL
.1 Ground fault personnel protection panel for pump circuits rated for 20 hp at 208 V and 50 hp at 600 V, 3 phase grounded supply with following features:
.1 Test button, ground indicator light, reset button.
.2 Line and load terminal blocks and control terminal block for wiring to starter control.

.3 Unit sensitivity: 10 mA.

.4 CSA Enclosure 1, surface mounted.

.5 Contact rating: 5 A, 120 V, 60 Hz.

.6 Fused resistive type artificial neutral.
Part 3 Execution
3.1 INSTALLATION
.1 Do not ground neutral on load side of ground fault relay.
.2 Pass phase conductors including neutral through zero sequence transformers.

.3 Connect supply and load wiring to equipment in accordance with manufacturer's recommendations.

3.2 FIELD QUALITY CONTROL
.1 Perform tests in accordance with Section 26 05 00 - Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements. 
.2 Arrange and pay for field testing of ground fault equipment by ground fault equipment manufacturer before commissioning service.

.3 Demonstrate simulated ground fault tests.

END OF SECTION 
Ver. 10/22

