NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
 Section 26 32 13.01 – Power Generation Diesel 
Page 1 of 16

Part 1 General

1.1 SECTION INCLUDES
.1 Diesel engine driven generator sets above 30kW rating, normally 3 phase, 120/208V 600V from 250 to 750kVA and 2400V delta or 2400/4160V star above 750kVA.
1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 78 00 - Closeout Submittals.

.3 Section 01 91 13.13 – Commissioning (Cx) Requirements.
.4 Section 23 11 13 – Facility Fuel-Oil Piping.

.5 Section 23 35 15 – Generator Exhaust.

.6 Section 26 05 00 – Common Work Results - Electrical.

.7 Section 26 32 03 – Installation of Power Generating Equipment. 
.8 Section 33 56 13 – Above Ground Fuel Storage Tanks. 

1.3 REFERENCES
.1 American National Standards Institute (ANSI)/American Petroleum Institute (API)
.1 ANSI/API 650, Welded Steel Tanks for Oil Storage Tenth Edition; Addendum 1.
.2 American National Standards Institute (ANSI)/National Electrical Manufacturers' Association (NEMA)
.1 ANSI/NEMA MG1, Motors and Generators.
.3 Canadian General Standards Board (CGSB)
.1 CAN/CGSB-3.6, Regular Sulphur Diesel Fuel.
.4 International Organization for Standardization (ISO)
.1 ISO 3046-1, Reciprocating Internal Combustion Engines - Performance - Part 1: Declarations of Power, Fuel and Lubricating Oil Consumptions, and Test Methods.
.5 National Electrical Manufacturers Association (NEMA)
.6 Underwriters' Laboratories of Canada (ULC)

.1 ULC-S601, Standard for Shop Fabricated Steel Aboveground Horizontal Tanks for Flammable and Combustible Liquids.
.2 ULC-S603, Steel above Ground Vertical Tanks for Flammable and Combustible Liquids.

1.4 SYSTEM DESCRIPTION
.1 Generating system consists of:
.1 Diesel engine.
.2 Alternator.

.3 Alternator control panel.

.4 Automatic transfer equipment.

.5 Battery charger and battery.

.6 Automatic engine room ventilation system.

.7 Fuel supply system.
.1 Fuel lines and fittings.

.2 Day tank

.3 Above ground fuel storage tank

.8 Exhaust system.

.9 Steel mounting base.

.10 Synchronizing panel as indicated.

.11 Manual by-pass isolation switch.

.2 System designed to operate as emergency standby unattended.  
1.5 EQUIPMENT SUPPLY AND INSTALLATION
.1 Supply and install components of the diesel engine driven generator set as noted.  Provide coordination with Division 22- Plumbing, Division 23 – Heating, Ventilation and Air Conditioning (HVAC) and Division 25 – Integrated Automation as required.  Refer to applicable sections here-in for additional scope of work related to each item.

.1 Diesel engine, alternator and radiator - supplied and installed by Division 26.

.2 Control panels - supplied and installed by Division 26. 

.3 Mounting base - supplied and installed by Division 26.

.4 Transfer switch - supplied and installed by Division 26.

.5 Day tank - supplied by Division 26 and installed by Division 22.

.6 Fuel lines and fittings - supplied and installed by Division 22 (including day tank fuel lines.) 

.7 Fuel Storage tanks – supplied and installed by Division 22. 
.8 Ventilation and Cooling System - supplied and installed by Division 23 and Division 25. (including remote radiator application)
.9 Exhaust system – supplied by Division 26, installed by Division 23. 
1.6 SUBMITTALS
.1 Include:

.1 Engine: make and model, with performance curves.
.2 Alternator: make and model.

.3 Voltage regulator: make, model and type.

.4 Automatic transfer switch: make, model and type.

.5 Manual bypass switch: make and model.

.6 Battery: make, type and capacity.

.7 Battery charger: make, type and model.

.8 Alternator control panel: make and type of meters and controls.

.9 Governor type and model.

.10 Automatic engine room ventilation system.
.11 Cooling air requirements in m3/s.

.12 British standard or DIN rating of engine.

.13 Flow diagrams for:

.1 Diesel fuel.
.2 Cooling air.

.14 Dimensioned drawing showing complete generating set mounted on steel base, including vibration isolators, exhaust system, drip trays, and total weight.
.15 Continuous full load output of set at 0.8 PF lagging.

.16 Description of set operation including:

.1 Automatic starting and transfer to load and back to normal power, including time in seconds from start of cranking until unit reaches rated voltage and frequency.
.2 Manual starting.

.3 Automatic shut down and alarm on:

.1 Overcranking.
.2 Overspeed.

.3 High engine temp.

.4 Low lube oil pressure.

.5 Short circuit.

.6 Alternator overvoltage.

.7 Lube oil high temperature.

.8 Over temperature on alternator.

.4 Manual remote emergency stop.
1.7 CLOSEOUT SUBMITTALS
.1 Provide operation and maintenance data for diesel generator for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.
.2 Include in Operation and Maintenance Manual instructions for particular unit supplied and not general description of units manufactured by supplier and:

.1 Operation and maintenance instructions for engine, alternator, control panel, automatic transfer switch, manual bypass switch, battery charger, battery, fuel system, engine room ventilation system, exhaust system and accessories, to permit effective operation, maintenance and repair.
.2 Technical data:

.1 Illustrated parts lists with parts catalogue numbers.
.2 Schematic diagram of electrical controls.

.3 Flow diagrams for:

.1 Fuel system.
.2 Lubricating oil.

.3 Cooling system.

.4 Certified copy of factory test results.
.5 Maintenance and overhaul instructions and schedules.

.6 Precise details for adjustment and setting of time delay relays or sensing controls which require on site adjustment.

1.8 WARRANTY
.1 Provide maintenance product warranty issued in the name of the Owner stating that the generating set is warranted against defects in material and workmanship for a period of 60 months, or 1500 operating hours, whichever occurs first, from date of substantial completion. 
1.9 MAINTENANCE MATERIALS
.1 Provide maintenance materials in accordance with Section 01 78 00 - Closeout Submittals.
.2 Include:
.1 2 fuel filter replacement elements.
.2 2 lube oil filter replacement elements.

.3 2 air cleaner filter elements.

.4 2 sets of fuses for control panel.

.5 Special tools for unit servicing.
1.10 Training
.1 Arrange and pay for on-site lectures and demonstrations by system manufacturer to train designated personnel in the use and maintenance of the generator set and transfer switch.

Part 2 Products
2.1 DIESEL ENGINE
.1 Diesel engine: to ISO 3046-1.
.1 Engine: standard product of current manufacture, from company regularly engaged in production of such equipment.
.2  Naturally aspirated and turbo charged, synchronous speed 1800 r/min, as indicated
.3 Capacity:

.1 Rated continuous power in kW at rated speed, after adjustment for system losses in auxiliary equipment necessary for engine operation; to be calculated as follows: Rated continuous output = Generator kW divided by Generator efficiency at full load.
.1 Under following site conditions:
.1 Altitude: as indicated in m.
.2 Ambient temperature: as indicated in degrees C.

.3 Relative humidity: as indicated in %.

.2 Engine overload capability 110% of continuous output for 1 hour within 12 hours period of continuous operation.
.4 Cooling System:
.1 Liquid cooled: heavy duty industrial radiator mounted on generating set base with engine driven pusher type fan to direct air through radiator from engine side, with ethylene glycol anti-freeze non-sludging above minus 46 degrees C. (edit to suit for remote radiator application)
.2 Air cooled: air cooling duct enveloping cylinder walls with pressure cooling by engine driven blower.

.3 To maintain manufacturer's recommended engine temperature range at 10% continuous overload in ambient temperature of 40 degrees C.

.4 Block heater: thermostatically controlled lube oil or liquid coolant heater connected to line side of automatic transfer switch to allow engine to start in room ambient 0 degrees C.

.1 Switch and fuse in heater circuit, mounted in engine-alternator control cubicle and fed from line side of automatic transfer switch.
.5 Fuel:
.1 Type A fuel oil: to CAN/CGSB-3.6.
.2 Arctic Grade diesel and diesel number 2:  to CANGSB-3.6.
.6 Fuel system: solid injection, mechanical fuel transfer pump, fuel filters and air cleaner, fuel rack solenoid energized when engine running.
.7 Governor:
.1 Mechanical hydraulic with:
.1 Steady state speed band of plus or minus 0.5%.
.2 Speed regulation no load to full load 5% maximum.

.3 Electronic load sharing type, electric actuator, speed droop externally adjustable from isochronous to 5%, temperature compensated with steady state speed maintenance capability of plus or minus 0.25%.

.8 Lubrication system:
.1 Pressure lubricated by engine driven pump.
.2 Lube oil filter: replaceable, full flow type, removable without disconnecting piping.

.3 Lube oil cooler.

.4 Engine sump drain valve.

.5 Oil level dip-stick.

.9 Starting system:
.1 Positive shift, gear engaging starter 12 or 24V dc.
.2 Cranking limiter to provide 3 cranking periods of 10s duration, each separated by 5 s rest.

.3 Lead acid, 12 or 24V storage battery with sufficient capacity to crank engine for 1min at 0 degrees C without using more than 25% of ampere hour capacity.

.4 Battery charger: constant voltage, solid state, two stage from trickle charge at standby to boost charge after use. Regulation: plus or minus 1% output for plus or minus 10% input variation. Automatic boost for 6h every 30 days. Equipped with dc voltmeter, dc ammeter and on-off switch. Minimum charger capacity: 7 A.

.10 Vibration isolated engine instrument panel with:
.1 Lube oil pressure gauge.
.2 Lube oil temperature gauge.

.3 Lube oil level gauge.

.4 Coolant temperature gauge.

.5 Coolant level gauge.

.6 Running time meter: non-tamper type.

.11 Guards to protect personnel from hot and moving parts. Locate guards so that normal daily maintenance inspections can be undertaken without their removal.
.12 Drip tray.

2.2 ALTERNATOR
.1 Alternator: to ANSI/NEMA MG1.
.2 Rating: 3phase, 60Hz, at 0.8PF, voltage and Kw rating as indicated on the electrical drawings.

.3 Output at 40 degrees C ambient:

.1 100% full load continuously.
.2 110% full load for 1h.

.3 150% full load for 1 min.

.4 Revolving field, brushless, single bearing.
.5 Drip proof.

.6 Amortisseur windings.

.7 Synchronous type.

.8 Dynamically balanced rotor permanently aligned to engine by flexible disc coupling.
.9 Exciter: rotating brushless.  

.10  NEMA class H insulation on windings.
.11  Thermistors embedded in stator winding and connected to alternator control circuitry.

.12 Voltage regulator: thyristor controlled rectifiers with phase controlled sensing circuit:
.1 Stability: 5 % maximum voltage variation at any constant load from no load to full load.
.2 Regulation: 5% maximum voltage deviation between no-load steady state and full-load steady state.

.3 Transient: 20 % maximum voltage dip on one-step application of 0.8PF full load.

.4 Transient: 3 % maximum voltage rise on one-step removal of 0.8PF full load.

.5 Transient: 5 s maximum voltage recovery time with application or removal of 0.8PF full load.

.13 Alternator: capable of sustaining 300% rated current for period not less than 10s permitting selective tripping of down line protective devices when short circuit occurs.
2.3 CONTROL PANEL
.1 Totally enclosed, engine mounted, mounting base isolated from diesel generator.
.2 Instruments:

.1 Analogue or Digital as indicated 100% solid state circuitry indicating type 2 % accuracy, rectangular face, flush panel mounting:
.1 Voltmeter: ac, scale 0 to 208 or 600 V as indicated.
.2 Ammeter: ac, scale 0 to 200 A, as indicated. (edit to suit)
.3 Wattmeter scale 0 to 200 kW as indicated. (edit to suit)
.4 Frequency meter: scale 55 to 65Hz.
.2 Voltmeter selector switch, rotary, panel mounting, round notched handle, four positions, labelled "Off-Phase A-Phase B-Phase C".
.3 Ammeter selector switch, rotary, maintained contacts, panel mounting, designed to prevent opening of current circuits, round notched handle, four position labelled "OFF- Phase A-Phase B-Phase C".

.4 Instrument Transformers

.1 Potential-dry type for indoor use:
.1 Ratio: 600 to 120 or as indicated.
.2 Rating: 600 V, 60Hz, BIL 5 kV.

.2 Current-dry type for indoor use:
.1 Ratio: 200 to 5 or as indicated.
.2 Rating: 600 V, 60Hz, BIL 5 kV.

.3 Positive action automatic short-circuiting device in secondary terminals.

.3 Controls:
.1 Engine start button.
.2 Selector switch: Off-Auto-Manual. 
.3 Engine emergency stop button and provision for remote emergency stop button.

.1 Alternator output breaker:
.1 Circuit breaker: bolt-on, moulded case, temperature compensated for 40 degrees C ambient, dual thermal-magnetic trip.
.2 Circuit breaker, solid state sensing with:

.1 Frame containing breaker contacts, arc quenchers, manual mechanism, quick- make, quick-break, spring-loaded overcenter switching mechanism, mechanically trip free from handle, fixed type.
.2 Static sensor: current monitors detect overload, short-circuit and ground-fault currents, and send these signals through solid-state circuits to static sensor which acts to trip breaker. Adjustable for current values and time of tripping.

.3 Flux-transfer shunt trip- magnetic tripping device actuated by signal from static sensor to open breaker contacts. Requires no external source of power.

.2 Voltage control rheostat: mounted on inside of control panel.
.3 Operating lights, panel mounted:

.1 "Normal power" pilot light.
.2 "Emergency power" pilot light.

.3 Green pilot lights for breaker on and red pilot lights for breaker off.

.4 Solid state indicator lights for alarm with 2 sets manually reset NO/NC contacts wired to terminal block for remote annunciation on:
.1 Low fuel level.
.2 Low battery voltage.

.3 Ventilation failure.

.4 Low coolant temperature.

.5 Solid state controller for automatic shutdown and alarms with 2 sets manually reset NO/NC contacts wired to terminal block for remote annunciation on:
.1 Engine overcrank.
.2 Engine overspeed.

.3 Engine high temperature.

.4 Engine low lube oil pressure.

.5 Short circuit.

.6 AC over voltage.

.6 Lamp test button.
.7 Synchronization and load sharing.
.8 Provision for remote monitoring.

2.4 AUTOMATIC TRANSFER SWITCH
.1 Refer to Section 26 36 23 – Automatic Transfer Switches. 
2.5 MANUAL BYPASS Isolation SWITCH
.1 Load break bypass and isolation switch: manually operated, double throw, to provide bypass around transfer switch to facilitate maintenance on diesel generator control panel and transfer switch. Switch lockable in bypass position.  Refer to Section 26 36 23 – Automatic Transfer Switches. 
2.6 STEEL MOUNTING BASE
.1 Complete generating set mounted on structural steel base of sufficient strength and rigidity to protect assembly from stress or strain during transportation, installation and under operating conditions on suitable level surface.
.2 Assembly fitted with vibration isolators and control console resiliently mounted.

.1 Spring type isolators with adjustable side snubbers and adjustable for levelling.
.3 Sound insulation pads for installation between isolators and concrete base.
2.7 EXHAUST SYSTEM
.1 Heavy duty industrial type horizontally mounted exhaust silencer with condensate drain, plug and welded couplings.
.2 Heavy duty flexible exhaust pipe with flanged couplings as required.

.3 Fittings and accessories as required.

.4 Expansion joints: stainless steel, corrugated, of suitable length, to absorb both vertical and horizontal expansion.
.5 Supplied by Division 26, installed by Division 23 as per Section 23 35 15 – Generator Exhaust.
2.8 FUEL SYSTEM
.1 Fuel storage tanks: ULC labelled.
.1 Above ground tank:  to ANS/Api 650 for field erected tanks.
.2 Above ground tank: to ULC-S601 and ULC-5630.
.2 Aboveground fuel storage tank: capacity in liters as indicated, mounted outdoors on elevated stand with fill and vent lines, fitted with weatherheads to Section 33 56 13 – Above Ground Fuel Storage Tanks.
.1 Electrically operated fuel transfer pump with float switch.

.3 Day tank:  capacity in liters as indicated, mounted indoors on elevated stand with fill and vent lines to exterior of building fitted with weatherheads.  Supplied by Division 26, installed by Division 22.

.4 Fuel level gauge and vent alarm, to Section 23 11 13 – Facility Fuel-Oil Piping.
.5 Drain and end plug.
.6 Feed and return lines, with flexible terminations at engine, to Section 23 11 13 – Facility Fuel-Oil Piping. 
.7 Shut-off cock, to Section 23 11 13 - Facility Fuel-Oil Piping.
.8 Renewable cartridge filter, to Section 23 11 13 - Facility Fuel-Oil Piping.
.9 Fire valve to Section 23 11 13 - Facility Fuel-Oil Piping.
.10 Isolating valves on lines serving auxiliaries to Section 23 11 13 - Facility Fuel-Oil Piping.
.11 Low fuel level alarm for remote indication to Section 23 11 13 - Facility Fuel-Oil Piping.

2.9 COOLING AIR SYSTEM
.1 Engine ventilating system, supplied and installed by Division 23 – Heating, Ventilation and Air Conditioning (HVAC) as indicated.
.1 Recirculating damper assembly with modulating motor.
.2 Cold air inlet damper assembly with modulating motor.

.3 Air discharge and intake gooseneck weatherhoods.

.4 Modulating thermostat.

.5 Replaceable air intake filters.

2.10 EQUIPMENT IDENTIFICATION
.1 Provide equipment identification in accordance with Section 26 05 00 – Common Work Results - Electrical.
.2 Control panel:

.1 Size 5 nameplates for controls including alternator breakers and program selector switch.
.2 Size 3 nameplates for meters, alarms, indicating lights and minor controls.

2.11 FABRICATION
.1 Shop assemble generating unit including:
.1 Base.
.2 Engine and radiator.

.3 Alternator.

.4 Control panel.

.5 Battery and charger.

.6 Automatic transfer equipment.

2.12 FINISHES
.1 Apply finishes in accordance with Section 26 05 00 – Common Work Results - Electrical.
.2 Alternator control cubicle: paint inside, exterior to match engine and alternator.

.3 Exhaust and inlet air hoods international orange.

.4 Other ducts and racks grey.

.5 Supply 0.25L of grey touch-up enamel.

2.13 SOURCE QUALITY CONTROL
.1 Factory test generator set including engine, alternator, control panels, transfer switch and accessories. 
.2 Provide certified copy of test results to Owner and incorporate into Commissioning Manual specified in Section 01 91 13.13 –Commissioning (Cx) Requirements. 
.3 Test procedure:

.1 Prepare blank forms and check sheet with spaces to record data. At top of first sheet record:
.1 Date.
.2 Generator set serial no.

.3 Engine, make, model, serial no.

.4 Alternator, make, model, serial no.

.5 Voltage regulator, make and model.

.6 Rating of generator set, kW, kV.A, V, A, r/min, Hz.

.2 Mark check sheet and record data on forms in duplicate as test proceeds.
.4 Tests:
.1 With 100% rated load, operate set for 23 h, taking readings at 30 min intervals, and record following:
.1 Time of reading.
.2 Running time.

.3 Ambient temp in degrees C.

.4 Lube oil pressure in kPa.

.5 Lube oil temp in degrees C.

.6 Engine coolant temp in degrees C.

.7 Exhaust stack temp in degrees C.

.8 Alternator voltage: phase 1, 2, 3.

.9 Alternator current: phase 1, 2, 3.

.10 Power in kW.

.11 Frequency in Hz.

.12 Power Factor.

.13 Battery charger current in A.

.14 Battery voltage.

.15 Alternator cooling air outlet temp.

.2 At end of 23 hours run increase load to 110% rated value, and take readings every 15 min for 1 hour.
.3 After completion of 24 hours run, demonstrate following shut down devices and alarms:

.1 Overcranking.
.2 Overspeed.

.3 High engine temp.

.4 Low lube oil pressure.

.5 Short circuit.

.6 Alternator overvoltage.

.7 Low battery voltage, or no battery charge.

.8 Manual remote emergency stop.

.9 High alternator temperature.

.4 Next install continuous strip chart recorders to record frequency and voltage variations during load switching procedures. Each load change delayed until steady state conditions exist. Switching increments to include:
.1 No load to full load to no load.
.2 No load to 70% load to no load.

.3 No load to 20% load to no load.

.4 20% load to 40% load to no load.

.5 40% load to 60% load to no load.

.6 60% load to 80% load to no load.

.5 Demonstrate:
.1 Automatic starting of set and automatic transfer of load on failure of normal power.
.2 Operation of manual bypass switch.

.3 Automatic shut down of engine on resumption of normal power.

.4 That battery charger reverts to high rate charge after cranking.

.6 Demonstrate low oil pressure and high engine temperature shutdown devices operation without subjecting engine to these excesses.
Part 3 Execution
3.1 INSTALLATION
.1 Refer to Section 26 32 03 – Installation of Electric Power Generating Equipment. 
.2 Locate generating unit and install as indicated.
.3 Install fuel supply system as indicated by Division 22.

.4 Install ventilating air duct system as indicated by Division 23 and Division 25.
.5 Install exhaust system as indicated by Division 23.

.6 Pipe muffler drains to nearest floor drain by Division 22.
.7 Complete wiring and interconnections as indicated.

.8 Start generating set and test to ensure correct performance of components.

3.2 FIELD QUALITY CONTROL
.1 Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.
.2 Notify Owner ten (10) working days in advance of test date.

.3 Provide fuel for testing and leave full tanks on acceptance.

.4 Demonstrate:

.1 Unit start, transfer to load, retransfer to normal power, unit shut down, on "Automatic" control.
.2 Unit start and shut down on "Manual" control

.3 Unit start and transfer on "Test" control.

.4 Unit start on "Engine start" control.

.5 Operation of manual bypass switch.

.6 Operation of automatic alarms and shut down devices.

.5 Run unit on load for minimum period of 8 hours to show load carrying ability, stability of voltage and frequency, and satisfactory performance of dampers in ventilating system to provide adequate engine cooling.
.6 At end of test run, check battery voltage to demonstrate battery charger has returned battery to fully charged state. Leave fuel tanks full on completion of tests.
end of section
Ver. 10/22

