NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 36 23 – Automatic Transfer Switches
Page 1 of 7

Part 1 General

1.1 SECTION INCLUDES
.1 Materials and installation for automatic load transfer equipment which can monitor voltage on all phases of normal power supply, initiate cranking of standby generator unit, transfer loads and shut down standby unit.
1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 78 00 - Closeout Submittals.
.3 Section 01 91 13.13 – Commissioning (Cx) Requirements. 
.4 Section 26 05 00 – Common Work Results - Electrical.
1.3 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CAN3-C13, Instrument Transformers.
.2 CSA C22.2 No.5, Moulded-Case Circuit Breakers, Molded-Case Switches and Circuit-Breaker Enclosures (Tri-national standard with UL 489, tenth edition, and the second edition of NMX-J-266-ANCE).

.3 CSA C22.2 No.178, Automatic Transfer Switches.

.2 American National Standards Institute (ANSI)/National Electrical Manufacturers Association (NEMA)
.1 ANSI/NEMA ICS 2, Industrial Control and Systems: Controllers, Contactors, and Overload Relays, Rated Not More Than 2000 Volts AC or 750 Volts DC.
1.4 SYSTEM DESCRIPTION
.1 Automatic load transfer equipment to:
.1 Monitor voltage on phases of normal power supply.
.2 Initiate cranking of standby generator unit on normal power failure or abnormal voltage on any one phase below preset adjustable limits for adjustable period of time.

.3 Transfer load from normal supply to standby unit when standby unit reaches rated frequency and voltage pre-set adjustable limits.  

.4 Transfer load from standby unit to normal power supply when normal power restored, confirmed by sensing of voltage on phases above adjustable pre-set limit for adjustable time period.  

.5 Shut down standby unit after running unloaded to cool down using adjustable time delay relay.

1.5 SUMBITTALS
.1 Include:

.1 Make, model and type.
.2 Load classification:

.1 Tungsten lamp load: as indicated in kW.
.2 Ballast lamp load: as indicated in kW.

.3 Motor load: as indicated in kW.

.4 Restricted use: resistance and general loads, 0.8pf or higher as indicated in kW.

.3 Single line diagram showing controls and relays.
.4 Description of equipment operation including:

.1 Automatic starting and transfer to standby unit and back to normal power.
.2 Test control.

.3 Manual control.

.4 Automatic shutdown.

1.6 CLOSEOUT SUBMITTALS
.1 Provide operation and maintenance data for automatic load transfer equipment for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.   
.2 Detailed instructions to permit effective operation, maintenance and repair.

.3 Technical data:

.1 Schematic diagram of components, controls and relays.
.2 Illustrated parts lists with parts catalogue numbers.

.3 Certified copy of factory test results.

Part 2 Products
2.1 MATERIALS
.1 Instrument transformers: to CAN3-C13.
.2 Contactors: to ANSI/NEMA ICS2.

2.2 CONTACTOR TYPE TRANSFER EQUIPMENT
.1 Contact Type Transfer Equipment: to CSA C22.2 No.178.
.2 Two- 3 phase contactors mounted on common frame, in double throw arrangement, mechanically and electrically interlocked, motor operated, with CSA sprinkler proof enclosure, as indicated.

.3 Rated: 600 V, 60Hz, 200 A (edit to suit), 4 wire, solid neutral as indicated on electrical drawings. 
.4 Main contacts: silver surfaced, protected by arc disruption means.

.5 Switch and relay contacts, coils, spring and control elements accessible for inspection and maintenance from front of panel without removal of switch panel or disconnection of drive linkages and power conductors.  Provide complete bypass – isolation type switch.
.6 Auxiliary contact: silver plated, to initiate emergency generator start-up on failure of normal power.

.7 Fault withstand rating: as required in kA symmetrical for 3 cycles.  
.8 Lever to operate switch manually when switch is isolated.

.9 Solid neutral bar, rated: as indicated.  
.10 Overlapping neutral contacts on contactor type transfer equipment.

.11 Solid state electronic in phase monitor as indicated. 
2.3 CONTROLS
.1 Selector switch - four position “Test", "Auto", "Manual", "Engine start".
.1 Test position - Normal power failure simulated. Engine starts and transfer takes place. Return switch to "Auto" to stop engine.
.2 Auto position - Normal operation of transfer switch on failure of normal power; retransfers on return of normal voltage and shuts down engine.

.3 Manual position - Transfer switch may be operated by manual handle but transfer switch will not operate automatically and engine will not start.
.4 Engine start position - Engine starts but unit will not transfer unless normal power supply fails. Switch must be returned to "Auto" to stop engine.

.2 Control transformers: dry type with 120V secondary to isolate control circuits from:
.1 Normal power supply.
.2 Emergency power supply.

.3 Relays: continuous duty, industrial control type, with wiping action contacts rated 10 A minimum:
.1 Voltage sensing: 3 phase for normal power and on one phase only for emergency, solid state type, adjustable drop out and pick up, close differential, 2V minimum undervoltage and over voltage protection.
.2 Time delay: normal power to standby, adjustable solid state, 0 to 60s. 
.3 Time delay on engine starting to override momentary power outages or dips, adjustable solid state, 0 to 60s delay.

.4 Time delay on retransfer from standby to normal power, adjustable 0-60s.  

.5 Time delay for engine cool-off to permit standby set to run unloaded after retransfer to normal power, adjustable solid state, 5s intervals to 180s.
.6 Time delay during transfer to stop transfer action in neutral position to prevent fast transfer, adjustable, 5s intervals to 180s.
.7 Frequency sensing, to prevent transfer from normal power supply until frequency of standby unit reaches preset adjustable values.

.4 Solid state electronic in-phase monitor as indicated.
.5 Switchable neutral pole on circuit breaker type equipment.

2.4 ACCESSORIES
.1 Pilot lights to indicate power availability normal and standby, switch position, green for normal, red for standby, mounted in panel.
.2 Plant exerciser: 168h timer to start standby unit once each week for selected interval but does not transfer load from normal supply. Timer adjustable 0-168h in 15 min intervals.
.3 Auxiliary relay to provide 1 N.O. and 1 N.C. contacts for remote alarms.

.4 Instruments:
.1 Analogue or Digital true rms, indicating type 2% accuracy, flush panel mounting:
.1 Voltmeter: ac, scale 0 to 600 V as indicated.
.2 Ammeter: ac, scale 0 to 200 A as indicated.
.3 Frequency meter: scale 55 to 65 Hz.

.5 Voltmeter selector switch: rotary, maintained contacts, panel mounting type, round notched handle, four position, labelled "OFF-Phase A-Phase B-Phase C".
.6 Potential transformers - dry type for indoor use:

.1 Ratio: 600 to 120.
.2 Rating: 600 V, 60Hz, BIL 5 kV.
.3 Accuracy rating: 2%.
.7 Ammeter selector switch: rotary, maintained contacts, panel mounting type, designed to prevent opening of current circuits, round notched handle, four position labelled "OFF - Phase A - Phase B - Phase C".
.8 Current transformers - dry type for indoor use:

.1 Ratio: as indicated.
.2 Rating: 600 V, 60Hz, BIL 5 kV.

.3 Accuracy rating: 2%.
.4 Positive action automatic short- circuiting device in secondary terminals.

.9 Manual bypass: c/w unit to isolate switch for maintenance purposes.
2.5 EQUIPMENT IDENTIFICATION
.1 Provide equipment identification in accordance with Section 26 05 00 – Common Work Results - Electrical. 
.2 Control panel:

.1 For selector switch and manual switch: size 5 nameplates.
.2 For meters, indicating lights, minor controls: size 3 nameplates.

.3 Nameplates to include: voltage, amperage and # of phases. 
2.6 SOURCE QUALITY CONTROL
.1 Complete equipment, including transfer mechanism, controls, relays and accessories factory assembled and tested.
.2 Tests:

.1 Operate equipment both mechanically and electrically to ensure proper performance.
.2 Check selector switch, in modes of operation Test, Auto, Manual, Engine Start and record results.

.3 Check voltage sensing and time delay relay settings.

.4 Check:

.1 Automatic starting and transfer of load on failure of normal power.
.2 Retransfer of load when normal power supply resumed.

.3 Automatic shutdown.

.4 In-phase monitor operation. 
.3
Provide copy of test reports and include with Commissioning Manual as per Section 01 91 13.13 – Commissioning (Cx) Requirements. 
Part 3 Execution
3.1 INSTALLATION
.1 Locate, install and connect transfer equipment.
.2 Check relays, solid state monitors and adjust as required.

.3 Install and connect battery and remote alarms.

3.2 FIELD QUALITY CONTROL
.1 Perform tests in accordance with Section 26 05 00- Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.
.2 Energize transfer equipment from normal power supply.

.3 Set selector switch in "Test" position to ensure proper standby start, running, transfer, retransfer. Return selector switch to "Auto" position to ensure standby shuts down.

.4 Set selector switch in "Manual" position and check to ensure proper performance.
.5 Set selector switch in "Engine start" position and check to ensure proper performance. Return switch to "Auto" to stop engine.

.6 Set selector switch in "Auto" position and open normal power supply disconnect. Standby should start, come up to rated voltage and frequency, and then load should transfer to standby. Allow to operate for 10 min, then close main power supply disconnect. Load should transfer back to normal power supply and standby should shutdown.

.7 Repeat, at 1h intervals, 3 times, complete test with selector switch in each position, for each test.

END OF SECTION

Ver. 10/22

