NL Master Specification Guide

for Public Funded Buildings

Section 26 41 00.02 – Secondary Lightning
Re-Issued 2021/05/31
 Arresters
Page 1 of 2

Part 1 General

1.1 SECTION INCLUDES
.1 Equipment and installation for secondary lighting arresters.
1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 91 13.13 – Commissioning (Cx) Requirements.
1.3 REFERENCES
.1 American National Standards Institute /Institute of Electrical and Electronics Engineers (ANSI/IEEE)
.1 ANSI/IEEE C62.41, Practice on Surge Voltages in Low-Voltage AC Power Circuits.
.2 Underwriters' Laboratories of Canada (ULC)
.1 UL 1449, Standard for Surge Protective Devices.
Part 2 Products
2.1 EQUIPMENT
.1 Arrester component parts: to ANSI/IEEE C62.41 and UL 1449.
.2 Arrester characteristics:

.1 System voltage: 600. 
.2 Rated voltage of arrester: 650 V.

.3 Indoor type.

Part 3 Execution
3.1 INSTALLATION
.1 Install arresters in switchboard and connect to secondary bus and ground bus.
END OF SECTION

Ver. 10/22

