NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2020/08/28
Section 26 50 00 – Lighting
Page 1 of 7

Part 1 General

1.1 References
.1 American National Standards Institute (ANSI)
.1 ANSI C82.1, Electric Lamp Ballasts-Line Frequency Fluorescent Lamp Ballast.
.2 ANSI C82.4, Ballasts for High-Intensity-Discharge and Low-Pressure Sodium Lamps.

.2 American National Standards Institute/Institute of Electrical and Electronics Engineers (ANSI/IEEE)
.1 ANSI/IEEE C62.41, Surge Voltages in Low-Voltage AC Power Circuits.
.3 American Society for Testing and Materials (ASTM)
.1 ASTM F1137, Specification for Phosphate/Oil and Phosphate/Organic Corrosion Protective Coatings for Fasteners.
.4 United States of America, Federal Communications Commission (FCC)
.1 FCC (CFR47) EM and RF Interference Suppression.
1.2 Related Sections
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 45 00 - Quality Control.
.3 Section 01 91 13.13 – Commissioning (Cx) Requirements.
1.3 SUBMITTALS
.1 Submit complete photometric data prepared by independent testing laboratory for luminaires where specified, for review by Owner.  

.2 Photometric data to include: VCP Table and spacing criterion and luminaire coefficient of utilization (CU) tables.
.3 Provide manufacturer's printed product literature, specifications and datasheet and include product characteristics, performance criteria, physical size, finish and limitations.
.4 Quality assurance submittals: provide the following in accordance with Section 01 45 00 - Quality Control.
.1 Manufacturer's instructions: provide manufacturer's written installation instructions and special handling criteria, installation sequence, cleaning procedures and relamping schedule.
.5 Submit product literature for each type of lamp supplied, complete with the mercury content of each lamp.
1.4 Delivery, Storage and Handling
.1 Deliver, store and handle materials in accordance with Section 01 61 00 - Common Product Requirements.
.2 Deliver materials to site in original factory packaging, labelled with manufacturer's name, address.
.3 Divert unused metal materials from landfill to metal recycling facility.
.4 Disposal and recycling of fluorescent lamps as per local regulations.
.5 Disposal of old PCB filled ballasts.
1.5 AcceptaBLE PRODUCTS 
.1 Luminaires described in the Lighting Fixture Schedule identify quality, performance criteria and other parameters, as indicated for this project. Named fixtures are acceptable with modifications and accessories, as indicated.

.2 Fixtures from other manufacturers may be acceptable provided:

.1 Appearance and lighting performance are similar.

.2 Quality is equal or better.

.3 Lamp and ballast criteria remain the same.

.4 The fixture is provided with modifications and accessories to provide a complete product in keeping with the intent of the project.

.5 Approval in writing is obtained from the Owner to the supplier/manufacturer five (5) days prior to tender closing date. 
Part 2 Products
2.1 Lamps
.1 Incandescent lamps to be - clear, A19, 100 Watt with 1000 hour lamp life, rough-service rated; or as indicated.
.2 Tungsten halogen lamps to be - clear, T-3, 300 Watt, RSC base, 2000 hour lamp life, 5000 lumens; or as indicated.
.3 Fluorescent lamps  to be - T8, 32 Watt, medium bi-pin, rapid or instant start to suit application, 4100 K, 30,000 hour lamp life, 2950 initial lumens, CRI 80; or as indicated.
.4 Metal halide lamps to be - clear, BT37, 400 Watt, mogul base, horizontal burn, 4100 K, 15,000 hour lamp life, 36,000 initial lumens, CRI65, open or enclosed type to suit the luminaire; or as indicated.
.5 Low pressure sodium lamps to be - clear, T21, 135 Watt, BY22d base, horizontal burn,16,000 hour lamp life, 22,000 initial lumens; or as indicated.
.6 High pressure sodium lamps to be - clear, ED18, 400 Watt, mogul base, 30,000 hour lamp life, 54,000 initial lumens; or as indicated.
.7 Compact fluorescent lamps to be - 18 Watt, G24q-2 base, 12,000 hour lamp life, 12,000 initial lumens, 4100 K, CRI 80; or as indicated.
.8 LED, as indicated.
2.2 Ballasts
.1 Fluorescent ballast: CBM and CSA certified, energy efficient type, IC electronic. 
.1 Rating: 120 or 347 V, 60 Hz, as indicated, for use with 2-32W, T8 octron imperial lamps. 
.2 RFI/EMI suppression circuit to: FCC (CFR47) Part 18, sub-part C, Class A and Part 15, sub-part B, Class B.

.3 Totally encased and designed for 40 °C ambient temperature.

.4 Power factor: minimum 98 % with 98% of rated lamp lumens.

.5 Crest factor: 1.5 maximum.

.6 Capacitor: thermally protected.

.7 Thermal protection: non-resettable on coil.

.8 Harmonics: 10 % maximum THD. 

.9 Operating frequency of electronic ballast: 20 khz minimum.

.10 Total Circuit Power: 62 Watts.

.11 Ballast Factor: greater than 0.90.

.12 Sound rated: Class A.

.13 Mounting: integral with luminaire.
.14 Be warranted by manufacturer for five years. 
.2 Metal halide ballast: design B.
.1 Rating:  60 Hz voltage as indicated, for use with metal halide lamp as indicated. Provide circuitry for standby light to provide light for starting and restart.
.2 Totally encased and designed for 40 °C ambient temperature.

.3 Power factor: minimum 95 % with 95% of rated lamp lumens.

.4 Type: constant wattage auto-transformer or solid state. 

.5 Input voltage range: plus or minus 10% of nominal.

.6 Minimum starting temperature: minus 29 °C at 90% line voltage.

.7 Mounting: outdoor integral with luminaire.

.8 Current crest factor: 1.7 maximum current.

.3 High pressure sodium ballast: to ANSI C82.4 design C.
.1 Rating: 60Hz voltage as indicated, for use with high pressure sodium lamps, as indicated.
.2 Totally encased and designed for 40 °C ambient temperature.

.3 Power factor: minimum 95 % with 95% of rated lamp lumens.

.4 Type: reactor or solid state with matching igniter as recommended by manufacturer.

.5 Input voltage range: plus 10% to minus 10% of nominal.

.6 Minimum starting temperature: minus 34 °C at 90% line voltage.

.7 Mounting: outdoor integral with luminaire.

.8 Current crest factor: 1.7 maximum current.

.4 Low pressure sodium ballast: design D.
.1 Rating: 60 Hz voltage as indicated, for use with low pressure sodium lamps as indicated.
.2 Totally encased and designed for 40 °C ambient temperature.

.3 Power factor: minimum 95% with 95% of rated lamp lumens.

.4 Type: constant wattage. 
.5 Input voltage range: plus or minus 20% of nominal.

.6 Minimum starting temperature: minus 34 °C at 90% line voltage.

.7 Mounting: outdoor integral with luminaire.
.5 LED drivers:
.1 General requirements:
.1 Designed for 10 year operational life while operating at maximum case temperature and 90 percent non-condensing relative humidity.
.2 Designed and tested to withstand electrostatic discharges without impairment of performance when tested according to IEC 61000-4-2.
.3 UL 8750 recognized or listed as applicable.
.4 Complies with IEC 61347-2-13 as applicable.
.5 Surge Tolerance: Designed and tested to withstand Category A surges of 4,000 V according to IEEE C62.41.2 without impairment of performance.
.6 Manufactured in a facility that employs ESD reduction practices in compliance with ANSI/ESD S20.20.
.7 Class A sound rating; inaudible in a 27 dBA ambient.
.8 No visible change in light output with a variation of plus or minus 10 percent line voltage input.
.9 Total Harmonic Distortion (THD): Less than 20 percent for loads greater than 25W; complies with ANSI C82.11.
.10 Drivers to track evenly across multiple lamp lengths and all light levels.
.11 Configuration tool available to optimize the following for LED fixtures:
.1 Light level.
.2 Efficacy.
.3 Thermal performance.
.2 3-wire control:
.1 Provide integral fault protection to prevent driver failure in the event of a mis-wire.
.2 Operate from input voltage of 120 V through 347 V at 60 Hz, or as indicated.
.3 Product(s):
.1 Maximum Inrush Current: Meets NEMA 410 inrush requirements.
.2 Constant Current Drivers:
.1 Support from 220 mA to 1.4 A to ensure a compatible driver exists.
.2 Support LED arrays up to 60W.
2.3 Finishes
.1 Light fixture finish and construction to meet ULC listings and CSA certifications related to intended installation.
2.4 Luminaires
.1 As indicated in luminaire schedule on drawings. Provide 10% spare lamps of each type noted in luminaire schedule. 
2.5 Optical Control Devices
.1 As indicated in luminaire schedule on drawings.
Part 3 Execution
3.1 Installation
.1 Locate and install luminaires as indicated. Install lamps in all fixtures.
.1 Provide adequate support to suit ceiling system.
3.2 Wiring
.1 Connect luminaires to lighting circuits.
.1 Install flexible conduit for vertical power supply drop to luminaires as indicated. Horizontal wiring using flexible conduit is not permitted.
3.3 Luminaire Supports
.1 For suspended ceiling installations support luminaires from ceiling grid in accordance with local inspection requirements.
3.4 Luminaire Alignment
.1 Align luminaires mounted in continuous rows to form straight uninterrupted line.
.2 Align luminaires mounted individually parallel or perpendicular to building grid lines.
3.5 FIELD QUALITY CONTROL
.1 Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.
END OF SECTION

Ver. 10/22

