NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 52 13.13 – Emergency Lighting 
Page 1 of 3

Part 1 General

1.1 SECTION INCLUDES
.1 Materials and installation for emergency lighting systems.
1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 91 13.13 - Commissioning (Cx) Requirements.
.3 Section 26 05 00 - Common Work Results – Electrical.
.4 Section 26 05 21 - Wires and Cables (0-1000 V).

.5 Section 26 05 34 - Conduits, Conduit Fastenings and Conduit Fittings.
1.3 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CSA C22.2 No.141, Unit Equipment for Emergency Lighting.
1.4 SUBMITTALS
.1 Data to indicate system components, mounting method, source of power and special attachments.

1.5 WARRANTY
.1 For batteries, the ten years warranty period is extended to 120 months, with no-charge replacement during the first five (5) years and pro-rate charge on the second five (5) years from the date of Substantial Completion.
Part 2 Products
2.1 EQUIPMENT
.1 Emergency lighting equipment: to CSA C22.2 No.141.
.2 Supply voltage: 120 V, ac.

.3 Output voltage: 12 or 24 V dc (edit to suit).
.4 Operating time: as required by the latest edition of the NBC (edit to suit).
.5 Battery: sealed, maintenance free.
.6 Charger: solid state, multi-rate, voltage/current regulated, inverse temperature compensated, short circuit protected with regulated output of plus or minus 0.01V for plus or minus 10% input variations.

.7 Solid state transfer circuit.

.8 Low voltage disconnect: solid state, modular, operates at 80% battery output voltage.

.9 Signal lights: solid state, for 'AC Power ON'. 

.10 Lamp heads: integral on unit and remote, 345 degrees horizontal and 180 degrees vertical adjustment. Lamp type: micro-tungsten or sealed beam as indicated. 

.11 Cabinet: suitable for direct or shelf mounting to wall and c/w knockouts for conduit. Removable or hinged front panel for easy access to batteries.

.12 Finish: standard.
.13 Auxiliary equipment:
.1 Test switch.

.2 Time delay relay.

.3 Battery disconnect device.

.4 AC input and DC output terminal blocks inside cabinet.

.5 Shelf.

.6 Cord and single twist-lock plug connection for AC.

.7 RFI suppressors.

2.2 WIRING OF REMOTE HEADS
.1 Conduit: type EMT, in accordance with Section 26 05 34 - Conduits, Conduit Fastenings and Conduit Fittings. 
.2 Conductors: RW90 type in accordance with Section 26 05 21 - Wires and Cables (0-1000 V) sized as indicated in accordance with manufacturer's recommendations. 

Part 3 Execution
3.1 INSTALLATION
.1 Install unit equipment and remote mounted fixtures.
.2 Direct heads.

.3 Connect exit lights to unit equipment.
.4 Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and in accordance with Section 01 91 13.13 – Commissioning (Cx) requirements.
END OF SECTION

Ver. 10/22

