NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2022/10/11
Section 26 52 13.16 – Exit Signs
Page 1 of 4 

Part 1 General
1.1 RELATED SECTIONS

.1 Section 01 33 00 - Submittal Procedures.

.2 Section 01 74 00 - Cleaning.

.3 Section 01 91 13.13 - Commissioning (Cx) Requirements. 

.4 Section 26 05 00 - Common Work Results – Electrical.
1.2 References
.1 Atomic Energy Control Board Regulations
.2 Canadian Code for Preferred Packaging

.3 Canadian Standards Association (CSA)

.1 CSA C22.2 No.141, Unit Equipment for Emergency Lighting.
.2 CSA C860, Performance of Internally-Lighted Exit Signs.

.4 National Fire Protection Association (NFPA) 
.1 NFPA 101, Life Safety Code.
1.3 Submittals
.1 Product Data:
.1 Submit manufacturer’s printed product literature, specifications and datasheets and include product characteristics, performance criteria, physical size, finish and limitations.
.2 Manufacturer’s Instructions: Provide to indicate special handling criteria, installation sequence, cleaning procedures and disposal.
Part 2 Products
2.1 Standard Units
.1 Exit lights: to CSA C22.2 No.141 and CSA C860, packaged in accordance with the Canadian Elecrtical Code for Preferred Packaging guidelines.
.2 Housing: cold rolled steel minimum 1.0 mm thick, satin aluminum enamel finish
.3 Face and back plates: extruded aluminum.

.4 Lamps: multiple - LED-12 W, 120 V, over 500,000 hours with average surface brightness of 3000 candela.

.5 Operation: designed for 25 years of continuous operation without relamping.

.6 Letters: 150 mm high x 19 mm, with 13 mm thick stroke red on extruded aluminum face, reading EXIT. 
.7 Downlight: white glass in bottom of unit.

.8 Third lamp socket for emergency lamp lighting circuit. 
.9 Face plate to remain captive for relamping.

2.2 Self-powered Units
.1 Exit lights: to CSA C22.2 No.141 and CSA C860, packaged in accordance with the Canadian Code for Preferred Packaging guidelines.
.2 Housing: cold rolled steel minimum 1.0 mm thick, satin aluminum enamel finish. 

.3 Face and back plates: extruded aluminum.

.4 Lamps: multiple - , LED-12W 120 V over 500,000 hours.

.5 Operation: designed for 25 years of continuous operation without relamping.

.6 Letters: 150 mm high x 19 mm wide, with 13 mm thick stroke, red on extruded aluminum face, reading EXIT. 
.7 Downlight: white glass in bottom of unit.

.8 Third lamp socket for emergency lamp lighting circuit. 
.9 Face plate to remain captive for relamping.

.10 Supply voltage: 120 V, ac.

.11 Output voltage: 12 or 24 V dc.

.12 Operating time:  minimum 30 minutes and as required by code.
.13 Recharge time: 12 hours

.14 Battery: sealed, maintenance free, warranty to Section 26 52 13.13 – Emergency Lighting, 1.5 – Emergency Lights.
.15 Charger: solid state, voltage/current regulated, inverse temperature compensated, short circuit protected, with regulated output of plus or minus 0.01 V for plus or minus 10% V input variation.

.16 Solid state transfer circuit.

.17 Signal lights: solid state, for 'AC Power ON'.  

.18 Lamp heads: integral on unit, 345° horizontal and 180° vertical adjustment. Lamp type: as indicated. 

.19 Mounting: suitable for universal mounting directly on junction box and c/w knockouts for conduit. Removable or hinged front panel for easy access to batteries.

.20 Cabinet: finish:  standard. 

.21 Auxiliary equipment:

.1 Lamp disconnect switch.

.2 Test switch.

.3 AC/DC output terminal blocks inside cabinet.

.4 RFI suppressor.

.5 Cord and single twist-lock plug connection for AC power supply.

2.3 Design X1
.1  Recessed, wall, end to wall, ceiling mounting as indicated.
.2  Single or double face with face plate to remain captive for relamping as indicated.

.3 Arrow: right or left as indicated. 

.4 Wireguard.

Part 3 Execution
3.1 Installation
.1 Install exit lights to manufacturer's recommendations, listing requirements, NFPA standard and local regulatory requirements.
.2 Connect fixtures to exit light circuits using RW90 wire in EMT conduit.

.3 Connect emergency lamp sockets to emergency circuits.
.4 Ensure that exit light circuit breaker is locked in on position.
.5 Provide tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements. 

3.2 CLEANING

.1 Proceed in accordance with Section 01 74 00 – Cleaning.
.2 On completion and verification of performance of installation, remove surplus materials, excess materials, rubbish, tools and equipment.
END OF SECTION

Ver. 10/22

