NL Master Specification Guide

for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 56 19 – Roadway Lighting
Page 1 of 3

Part 1 General

1.1 SECTION INCLUDES
.1 Materials and installation for concrete, steel, aluminum and wood lighting poles.
1.2 RELATED SECTIONS
.1 Section 01 33 00 - Submittal Procedures.
.2 Section 01 91 13.13 – Commissioning (Cx) Requirements.
.3 Section 26 05 00 – Common Work Results - Electrical.

.4 Section 26 50 00 - Lighting.
1.3 REFERENCES
.1 Canadian Standards Association (CSA)
.1 CSA C22.2 No.206, Lighting Poles.

.2 CAN/CSA-O15, Wood Utility Poles and Reinforcing Stubs.

.3 CSA O80 Series, Wood Preservation.

Part 2 Products
2.1 STEEL POLES
.1 Steel poles: to CSA C22.2 No.206 designed for underground wiring and:
.1 Mounting on concrete anchor base without transformer base.
.2 Style: monotube, minimum 3.0 mm thick, tapered round.
.3 Straight for one or two luminaire mounting brackets.
.4 Terminating in double curved davit for two luminaire mounting.
.5 Access handhole 900 mm above pole base for wiring connections, with welded-on reinforcing frame and bolted-on cover.

.6 Size:  as indicated. 

.7 Anchor bolts: galvanized steel with shims, nuts and covers, size and number as indicated. 
.8 Finish: flat black. 

.9 Grounding lug.

2.2 ALUMINUM POLES
.1 Aluminum poles: to CSA C22.2 No.206 designed for underground wiring and:
.1 Mounting on concrete anchor base without transformer base.
.2 Style: Monotube, round tapered G063-T6 aluminum, wall thickness 6 mm.

.3 Straight for one or two luminaire mounting brackets.

.4 Tapered davit for two luminaires.

.5 Access handhole 900 mm above pole base for wiring connections, with welded-on reinforcing frames bolted-on cover.

.6 Size: as indicated. 

.7 Anchor bolts: stainless steel with shims, nuts, washers and covers, as indicated.

.8 Finish: semi-lustrous satin by rotary sand process.

.9 Grounding lug.

2.3 WOOD POLES
.1 Wood poles: to CAN/CSA-O15, class 1 Eastern White cedar and:
.1 Length: as indicated
.2 Minimum diameter: at butt as indicated, at top as indicated.
.3 Pressure treated: to CSA O80.

2.4 LUMINAIRE MOUNTING BRACKETS
.1 Mounting brackets steel for specified luminaires:
.1 Single and twin brackets as indicated.
.2 Arm extension length: as indicated m.

.3 Type: cantilever double guy. 
.4 Single or double tapered davit type as required.

2.5 LUMINAIRES
.1 Luminaire with cast aluminum weatherproof housing and:
.1 Lamp type:  as indicated on Light Fixture Schedule shown on drawings. 
.2 Ballast: 347 V, one lamp, in accordance with Section 26 50 00 - Lighting. 

.3 Optical assembly:

.1 For metal halide, high pressure sodium or low pressure sodium lamps:
.1 Reflector: sheet aluminum with Alzak finish.
.2 Refractor: one piece prismatic virgin acrylic.

.3 Gasket: neoprene seal between refractor and housing.

.4 Light Distribution:
.1 IES distribution Type I, II, III, IV, V as indicated by adjusting position of lamp socket.
.5 Self-locking latches of stainless steel and aluminum.
.6 Factory wired including integral ballast terminated at terminal block.

Part 3 Execution
3.1 INSTALLATION
.1 Install poles true and plumb, complete with brackets in accordance with manufacturer's instructions.
.2 Install luminaires on pole davits and install lamps.

.3 Check luminaire orientation, level and tilt.

.4 Connect luminaire to lighting circuit.

.5 Perform tests in accordance with Section 26 05 00 - Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements. 

END OF SECTION

Ver. 10/22

