Date




     Project Number  


           Page 
 of 2






      Project Name

WST Master Specification

Section 16525 - Floodlighting - Exterior

NL Master Specification Guide
for Public Funded Buildings
Re-Issued 2021/05/31
Section 26 56 36 – Flood Lighting 
Page 1 of 2

Part 1 GENERAL

1.1 RELATED SECTIONS

.1 Section 01 33 00 – Submittals.
.2 Section 01 78 00 - Closeout Submittals.
.3 Section 01 91 13.13 - Commissioning (Cx) Requirements.

.4 Section 26 05 00 - Common Work Results – Electrical.

.5 Section 26 09 23.02 - Lighting Control Devices – Photoelectric.

.6 Section 26 50 00 - Lighting.
1.2 SUBMITALS
.1 Indicate vertical and horizontal beam spread, beam lumens, beam efficiency and complete photometric data as shown by independent laboratory tests.

.2 Computer printout for aiming angles.
.3 Submit product data sheets for outdoor weatherproof floodlighting. Include product characteristics, performance criteria, physical size, limitations and finish.
.4 Manufacturer’s Instructions: Provide to indicate special handling criteria, installation sequence and cleaning procedures.
1.3 Maintenance and Operation

.1 Provide maintenance and operation data for incorporation into manual specified in Section 01 78 00 – Closeout Submittals.
Part 2 PRODUCTS

2.1 DESIGN A

.1 Outdoor weatherproof floodlight:

.1 Housing die-cast aluminum formed and welded, epoxy painted socket housing. Integral watertight entrance bushing with rubber gland. Aluminum yoke with bolt hole for mounting accessories. Degree-marked vertical pre-aiming quadrant with repositioning stop to automatically return fixture to original setting after servicing. Anodised aluminum lens ring, gasket, and complete with stainless steel pressure clamps. Lens assembly captive to reflector by hinge. Cast aluminum rear relamping knob.

.2 Lens: lexan clear convex heat tempered, shock and impact resistant.

.3 Reflector: Alzak aluminum.

.4 Lamp: wattage and type as indicated with holder and socket to Section 26 50 00 - Lighting.

.5 Ballast: as indicated to Section 26 50 00 - Lighting.

.6 Photo-electric control: to Section 26 09 23.02 - Lighting Control Devices - Photoelectric.
Part 3 EXECUTION

3.1 INSTALLATION

.1 Install floodlights in accordance with manufacturer's instructions and as indicated.
.2 Aim energized floodlights as indicated during darkness and in presence of Owner.

.3 Lock floodlights in final aiming position after Owner’s approval.

.4 Operate floodlights for minimum 100 h for proper aging, then take illuminance measurements. Ensure compliance with design specifications and adjust aiming of luminaires as necessary.
3.2 FIELD QUALITY CONTROL 
.1 Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.
END OF SECTION

Ver. 10/22

