# GENERAL

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 78 00 - Closeout Submittals.

### Section 01 91 13.13 - Commissioning (Cx) Requirements.

### Section 26 05 00 - Common Work Results – Electrical.

### Section 27 10 05 – Structured Cabling for Communication Systems.

### Section 27 20 00 - Data Communications.

## REFERENCES

### Canadian Standards Association (CSA)

#### CAN/CSA-T530, Building Facilities, Design Guidelines for Telecommunications.

#### CAN/CSA-T529, Design Guidelines for Telecommunications Wiring System in Commercial Buildings.

#### CAN/CSA-C22.2 No. 214, Communications Cables.

#### CAN/CSA-C22.2 No. 182.4, Plugs, Receptacles, and Connectors for Communication Systems.

### Electronic Industries Association (EIA)

#### EIA/TIA Bulletin TSB-36, Technical Systems Bulletin Additional Cable Specifications for Unshielded Twisted Pair Cables.

#### ANSI/TIA-568-C.2, Balanced Twisted-Pair Telecommunications Cabling and Components, Category 6.

#### ISO/IEC 11801, Information Technology – Generic Cabling for Customer Premises, Edition 2, Class E.

## SYSTEM DESCRIPTION

### Structured system of telecommunications cables (copper and optical fibre) installed within buildings for distributing voice and data (including video) signals.

### Installed in physical star configuration with separate horizontal and backbone sub-systems. Horizontal cables link work areas to telecommunications closet located on same floor. Telecommunications closets linked to central equipment room by backbone cables.

# PRODUCTS

## STATION WIRE (ZSW)

### 4-pair, 23 or 24 AWG, 100 ohm cable with insulated copper conductor in separate outer jacket: to C22.2 No.214. FT-4 flame spread rating on jacket for riser cables in conduit systems, otherwise FT-6 flame spread rating on jacket for horizontal cable runs in plenum ceiling spaces.

### Voice-grade electrical transmission requirements: to CAN/CSA T529 and TSB-36, Category 6.

### Data-grade electrical transmission requirements to: ANSI/TIA-568-C.2, Category 6.

## SHIELDED TWISTED PAIR (STP) CABLE

### 2 pair 150 ohm cable: to CAN/CSA-T529.

## COMMUNICATIONS FLAT CABLE (CFC)

### 4 pair 22 AWG insulated copper conductors in separate flat outer jacket.

## COMMUNICATIONS BUILDING CABLE (CBC)

### 23 AWG insulated copper conductors grouped in 25-pair separately identified modules surrounded by metallic tape shield and covered with thermoplastic jacket: to CAN/CSA C22.2 No. 214 and CAN/CSA-T529. FT-4 and FT-6 flame rated jacket.

### Voice-grade electrical performance to: CAN/CSA T529.

## PREMISES COMMUNICATION CABLE (PCC)

### 22 AWG 100 ohm impedance insulated copper conductors grouped in 25-pair separately identified modules with metallic shield and surrounded with jacket: to C22.2 No. 214. FT-1 FT-4 and FT-6 flame rated jacket in plenum ceiling spaces.

### Electrical/transmission performance to: CAN/CSA-T529.

## COAXIAL CABLE (CXC)

### Coaxial members, 75 ohm impedance each having metallic centre conductor surrounded by dielectric material and metal outer conductors separated by dielectric material and surrounded by jacket: to CAN/CSA C22.2 No. 214. FT-4 and FT-6 flame rated jacket in plenum ceiling spaces.

### For data communications, 24 AWG, 50 ohm impedance. Electrical transmission performance: to CAN/CSA-T529.

### For cable television, 75 ohm impedance. Centre conductor No. 22 AWG solid; insulation of solid polyethylene shield of aluminum foil plus braid shield coverage 97%. Loss at 500 MHz not to exceed 3.5 dB per 30 m.

### For 50 ohm coaxial cable systems, type BNC connector for service outlet to: CAN/CSA-T529.

## OPTICAL/FIBRE CABLE (OFC)

### Number of pair as required tight buffer tube 50/125 micrometre multi-mode graded index fibre: to CAN/CSA T529.

# EXECUTION

## INSTALLATION OF HORIZONTAL DISTRIBUTION CABLES

### Install ZSW, STP, PCC, OFC, and CXC horizontal cables as indicated in conduits, cable troughs, underfloor ducts or ceiling space from termination in telecommunications closet to outlets.

### Terminate 1 ZSW cables per work station terminated in accordance with CAN/CSA C22.2 No.182.4 and CAN/CSA-T529, Figure 11-1.

### Terminate STP cable in accordance with CAN/CSA-T529.

### Install CFC cables under carpet from wall termination points.

#### 1 service outlet(s) terminated in accordance with C22.2 No.182.4 and CAN/CSA-T529, Figure 11-1.

#### Wall termination unit interconnecting ZSW to CFC wiring transition.

### For distribution of television signals, terminate CXC cable on type F connectors. For distribution of data signals, terminate CXC cable in accordance with CAN/CSA-T529.

### Terminate OFC cables with SC connectors.

## INSTALLATION OF BACKBONE CABLES

### Install CBC, OFC, CXC and ZSW cable as indicated in conduit from termination in each telecommunications closet to equipment room. Termination: to CAN/CSA-T529.

### Terminate CBC and ZSW cables in accordance with CAN/CSA-T529 on patch panel.

### For distribution of television signals, terminate CXC cable on type F connectors. For distribution of data signals, terminate CXC cable in accordance with CAN/CSA-T529.

### Terminate OFC cables on patch panel with SC connectors.

## FIELD QUALITY CONTROL

### Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Test UTP cable installations for using a Level IV tester. Refer to Section 27 10 50, sentence 3.4.3 for number and type of tests.

### Test optical fibre cables for:

#### End-to-end loss at 850 nm.

#### OTDR tests.

### Test coaxial cables for:

#### Continuity.

#### Attenuation at 20 MHz.

### Test STP cables for:

#### Continuity.

#### Attenuation at 20 MHz.

END OF SECTION