# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 78 00 - Closeout Submittals.

### Section 06 10 53 – Miscellaneous Rough Carpentry.

### Section 27 05 14 - Communication Cables Inside Buildings.

### Section 27 05 28 - Pathways for Communications Systems.

### Section 27 20 00 - Data Communications.

### Section 27 51 23 - Intercommunications and Program Systems.

## REFERENCES

### Canadian Standards Association (CSA)

#### CSA-C22.2 No. 214, Communications Cables (Bi-National standard with UL 444).

#### CSA-C22.2 No. 232, Optical Fiber Cables.

### Telecommunications Industry Association (TIA)/Electronic Industries Alliance (EIA)

#### ANSI/TIA-568-C.1, Commercial Building Telecommunications Cabling Standard, Part 1: General Requirements.

#### ANSI/TIA-568-C.2, Commercial Building Telecommunications Cabling Standard, Part 2: Balanced Twisted-Pair Cabling Components.

#### ANSI/TIA-568-C.3, Optical Fiber Cabling Components Standard.

#### TIA/EIA-606-A, Administration Standard for the Commercial Telecommunications Infrastructure.

#### TIA TSB-140, Telecommunications Systems Bulletin - Additional Guidelines for Field-Testing Length, Loss and Polarity of Optical Fiber Cabling Systems.

#### TIA-598-C, Optical Fiber Cable Color Coding.

## DEFINITIONS

### Refer to TIA/EIA-598-C, Annex A for definitions of terms: optical-fiber interconnect, distribution, and breakout cables.

## SYSTEM DESCRIPTION

### Structured telecommunications wiring system consist of unshielded-twisted-pair and optical fiber cables, terminations, connectors, cross-connection hardware and related equipment installed inside building for occupant's telecommunications systems, including voice (telephone), data, and image.

### Installed in physical star configuration with separate horizontal and backbone sub-systems.

#### Horizontal cables link work areas to telecommunications rooms located on same floor.

#### Telecommunications rooms linked to main terminal/equipment room (MT/ER) by backbone cables.

#### MT/ER also linked to Entrance Room by backbone cables.

## SUBMITTALS

### As-built Records and Drawings:

#### Provide Microsoft Access database reflecting cable installation and cross-connections.

#### Provide electronic drawings in AutoCAD format, latest edition, depicting all construction.

#### Provide two (2) bound complete hard-copy sets of as-built records to the Owner.

##### Provide and place one hard copy of as-built records for each telecommunications room in plan holder in each telecommunications room.

## QUALITY ASSURANCE

### Health and Safety Requirements: do construction occupational health and safety in accordance with Section 01 35 29.06 - Health and Safety Requirements.

# Products

## FOUR-PAIR 100 Ω BALANCED TWISTED PAIR CABLE

### Four-pair, 100 ohm balanced unshielded-twisted-pair (UTP) cable, flame test classification FT6 or MPP or CMP, FT4 or MPG or CMG to: CSA-C22.2 No. 214, Category 6 (Cat 6) to: ANSI/TIA-568-C.2.

## MULTI-PAIR 100 Ω BALANCED TWISTED PAIR CABLE

### 100 ohm, pairs, as indicated, sheath consists of thermoplastic jacket with underlying metallic shield, Category 5 to: ANSI/TIA-568-C.2, flame test classification FT4 or MPG or CMG to: CSA-C22.2 No. 214.

## WORK AREA UTP 4-PAIR MODULAR JACK

### Eight-position modular jack ("RJ-45"), type T568B Category 6 to: ANSI/TIA-568-C.2:

#### In self-contained surface-mount box.

#### Mounted in compatible double gang faceplate, flush entry.

### Multi-user telecommunications outlet assembly (MUTOA), each port equipped with factory installed "RJ-45" jacks, type T568B Category 6 to: ANSI/TIA-568-C.2.

## TERMINATION AND CROSS-CONNECTION HARDWARE FOR UTP

### IDC Terminal strips, 25 pair, for terminating multi pair 100 Ω balanced twisted pair cables and supporting cross-connections using jumper wires or compatible plug-ended patch cords: Category 6 to: ANSI/TIA-568-C.2.

### Mount or block for housing 10 IDC terminal strips, mounted on wall, rack or cabinet, as indicated.

#### Distribution rings or channels capable of externally mating with the above mount for managing cross-connection wires.

### Patch panel, 2 rack units high, ports as indicated.

#### Each port equipped with factory installed "RJ-45" jacks, type T568A Category 6 to: ANSI/TIA-568-C.2 for each cable run.

#### Horizontal cable-management unit for every 48 ports.

### Consolidation point, terminates 12 UTP horizontal cables from telecommunications room on IDC terminations. Cables extending to work areas terminate on IDC terminal strips RJ-45 jacks, type T568B. Category 6 to: ANSI/TIA-568-C.2.

## UTP CROSS-CONNECT WIRE

### Category 6, 4 pairs to: ANSI/TIA-568-C.2.

## UTP PATCH CORDS

### 2.0 meters long, with factory-installed male plug at one end to mate with "RJ-45" jack and with factory-installed male plug at other end to mate with "RJ-45" jack Category 6, 4 pairs to: ANSI/TIA-568-C.2.

## UTP EQUIPMENT CABLE

### 4 pair "cable", 2.0 meters long, with factory-installed male plug on one end to mate with "RJ-45" jack and other end equipped with factory-installed male plug to mate with "RJ-45" jack: Category 6 to: ANSI/TIA-568-C.2.

## UTP WORK AREA CORDS

### 3.0 meters long, each end equipped with "RJ-45" plug Category 6 to: ANSI/TIA-568-C.2.

## OPTICAL-FIBER CABLE

### Distribution, with conductive members, multi-mode 50/125, 500 MHz km capacity, 50/125, laser-optimized, 2000 MHz km capacity, 8.3 micron single mode, multi strands to: CSA-C22.2 No. 232 and ANSI/TIA-568-C.3, flame test classification FT6 or FT4, as indicated, each end terminated with duplex SC connectors.

## CONSOLIDATION POINT FOR OPTICAL FIBER

### Consolidation point, terminates 12 optical-fiber horizontal cables from telecommunications room on duplex SC compatible adapters.

## OPTICAL-FIBER CONNECTORS AT WORK AREA

### Faceplate equipped with Duplex SC compatible adapters to: ANSI/TIA-568-D.

## OPTICAL-FIBER PATCH PANEL

### Mounted on wall, in rack or cabinet as indicated, rack units, with lockable cover, capable of terminating sufficient fiber, equipped with duplex SC compatible adapters.

## OPTICAL-FIBER PATCH CORDS

### Interconnect cable, 2 strands, 2.0 meters long, each end equipped with duplex SC connectors. Multi-Mode 50/125, 500 MHz km capacity, 50/125, laser-optimized, 2000 MHz km capacity, or single mode to: ANSI/TIA-568-C.3.

## OPTICAL-FIBER WORK AREA CORDS

### Interconnect cable, 2 strands, 2.0 meters long, each end equipped with Duplex SC connectors. Multi-Mode 50/125, 500 MHz km capacity, 50/125, laser-optimized, 2000 MHz km capacity, or single mode to: ANSI/TIA-568-C.3.

# Execution

## INSTALLATION OF TERMINATION AND CROSS-CONNECT HARDWARE

### Install termination and cross-connect hardware on wall, in rack or in cabinet as indicated and according to manufacturers' instructions.  Identify and label as indicated to: TIA/EIA-606-A.

### Install consolidation points, as indicated according to manufacturer's instructions. Identify and label as indicated to: TIA/EIA-606-A.

## INSTALLATION OF HORIZONTAL DISTRIBUTION CABLES

### Install horizontal cables as indicated in conduits from telecommunication rooms to consolidation point. Identify and label as indicated to: TIA/EIA-606-A.

### Support horizontal cables at intervals not exceeding 1.0 meters.

#### Where raceways are used to distribute cables to each zone, provide supplementary "J" hooks to support cables at intervals not exceeding 1.0 meters.

### Install horizontal cables from consolidation point to individual work-area jacks.

#### Provide supplementary "J" hooks to support cables at intervals not exceeding 1.0 meters.

#### Identify and label as indicated to: TIA/EIA-606-A.

### Terminate horizontal cables in telecommunications room and at consolidation point.

#### Identify and label as indicated to: TIA/EIA-606-A.

### Harness slack cable in cabinets, racks, and wall-mounted termination and cross-connection hardware.

## INSTALLATION OF BACKBONE CABLES

### Install backbone cables from each telecommunications room to main terminal/equipment room (MT/ER) as indicated and according to manufacturers' instructions.

#### Identify and label as indicated to: TIA/EIA-606-A.

### Install backbone cables from MT/ER to carrier demarcation point in Entrance Room as indicated and according to manufacturer's instructions.

#### Identify and label as indicated to: TIA/EIA-606-A.

## INSTALLATION OF EQUIPMENT CABLES

### Install equipment cables from equipment terminal strips or patch panel as indicated.

#### Identify and label as indicated to: TIA/EIA-606-A.

## IMPLEMENT CROSS-CONNECTIONS

### Implement cross-connections using patch cords as specified.

## FIELD QUALITY CONTROL

### Test horizontal UTP cables as specified below and correct deficiencies provide record of results as hard copy and electronic record on CD.

#### Perform tests for Permanent Link on installed cables, including spares:

##### Category 5e using certified level IIe tester to: ANSI/TIA-568-C.1.

##### Category 6 using certified level III tester to: ANSI/TIA-568-C.2.

#### Perform tests for Permanent Link on 20% of cross-connected data horizontal cabling installed from each telecommunications room, including shortest and longest drops from each telecommunications room: should more than 5% of tested cables fail, test remaining cross-connected data cables.

##### Category 5e using certified level II tester to: ANSI/TIA-568-C.1.

##### Category 6 using certified level III tester to: ANSI/TIA-568-C.2.

### Test backbone UTP cables as specified below and correct deficiencies: provide record of results as hard copy and electronic record on CD.

#### Perform tests for Permanent Link on 4-pair cables:

##### Category 5e using certified level II tester to:  ANSI/TIA-568-C.1.

##### Category 6 using certified level III tester to:  ANSI/TIA-568-C.2.

#### Perform Wire Map tests on multi-pair UTP cables to: ANSI/TIA-568-C.1.

### Test Optical-fiber strands for attenuation to: ANSI/TIA-568-C.1 and correct deficiencies:  provide record of results as hard copy and electronic record on CD.

#### Test horizontal links at only one wavelength (850 nm or 1300 nm) and in one direction.

##### Attenuation to be less than 2.0 dB, unless consolidation point is used.

##### If consolidation point is used, attenuation test result to be less than 2.75 dB when testing between horizontal cross-connect and telecommunications outlet/connector.

#### Test backbone links in both directions.  Backbone links:

##### Test multi-mode fiber at both applicable wavelengths (850 nm and 1300 nm).

##### Test single-mode fiber at both applicable wavelengths (1550 nm and 1310 m).

#### Maximum attenuation: Cable attenuation + Connector loss + Splice loss.

##### Multi-mode-fiber attenuation coefficients:

###### 3.5 db/km @ 850 nm; and

###### 1.5 db km @ 1300 nm

##### Single-mode fiber attenuation coefficients at both 1310 nm and 1550 nm:

###### 1.0 db/km for inside plant cable; and

###### 0.5 db/km for outside plant cables.

##### Maximum connector insertion loss: 0.75 db per pair and maximum splice insertion loss: 0.3 db.

### Perform additional Tier 2 tests using optical time domain reflectometer (OTDR) on backbone fiber pairs to: TSB-140.

#### Correct deficiencies.

#### Provide record of results as described in SUBMITTALS.

### Provide record of results as hard copy and electronic record on CD to: TIA/TSB-140.

END OF SECTION