# General

## SECTION INCLUDES

### Materials and installation for telephone drop and underground, coaxial and optical-fibre cable terminals.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 - Construction/Demolition Waste Management And Disposal.

## REFERENCES

### Canadian Standards Association (CSA International)

#### CSA C22.2 No.214-02, Communications Cables (Bi-national standard, with UL 444).

#### CSA T530-99, Commercial Building Standard for Telecommunications Pathways and Spaces (Adopted ANSI/TIA/EIA-569-A).

## DESIGN REQUIREMENTS

### Entrance facility: to CSA T530 and CSA C22.2 No.214.

## PRODUCT DATA

### Submit product data in accordance with Section 01 33 00 - Submittal Procedures.

## WASTE MANAGEMENT AND DISPOSAL

### Separate and recycle waste materials in accordance with Section 01 74 19 - Construction/Demolition Waste Management and Disposal.

### Remove from site and dispose of all packaging materials at appropriate recycling facilities.

### Collect and separate for disposal paper plastic polystyrene corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal and wiring materials from landfill to metal recycling facility as approved by Engineer Consultant.

### Fold up metal banding, flatten and place in designated area for recycling.

# Products

## TELEPHONE DROP CABLE TERMINALS

### Individual drop cable terminal block: 2 line terminals, one ground terminal and carbon block 150 micrometre gap lightning protectors with fuse, with housing designed for outside or interior mounting as indicated.

### Multiple drop cable 25 pairs terminal block: carbon block gap lightning protectors with fuse, with housing designed for outside or interior mounting.

### Terminal blocks where lightning protection is not required: 2, 3 or 12 line terminals, one ground terminal with housing designed for outside or interior mounting as indicated.

## UNDERGROUND TELEPHONE CABLE TERMINALS

### Buried cable terminal for buried cables: base plate, cylindrical weatherproof housing, approximately 305 x 460 mm, terminal strips with binding posts and connectors for 25 pairs.

### Cable terminals for buried cables at reel ends: basic terminal designed to be driven into ground, weatherproof cover approximately 1015 mm from base to top, 2 pair terminal blocks as required, ground clamps and adhesive "ATTENTION" signs and numerals to identify cable circuits.

## COAXIAL CABLE TERMINAL

### Outer connector nut, inside threaded, sliding over body of terminal.

### Terminal body, inside threaded, designed to screw on to outer sheath of cable.

## OPTICAL-FIBRE TERMINAL

### For large installations, fibre distribution frame consisting of 2.13 m x 0.48 m equipment rack containing end and foot caps, fibre routing guides, horizontal jumper troughs and

#### Connector module housings with transparent hinged door, each CMH equipped with SC connectors.

#### Splice module housings each equipped with splice trays for single-mode, multi-mode fibre, fusion, or mechanical splice as indicated.

### For smaller installations, wall mounted self-contained interconnect unit equipped with SC connectors, without splice tray.

# Execution

## INSTALLATION

### Install drop cable terminals outside and inside in accordance with manufacturer's instructions. Connect drop cable conductors to terminals and run ground conductor from ground terminal to building electrical system ground.

### Install buried cable terminals. Connect conductors in accordance with manufacturer's instructions. Replace weatherproof housing.

### Drive Z wire terminals into ground until base is flush with ground surface. Install cable, fasten to ground clamps and connect to terminal blocks in accordance with manufacturer's instructions.

### Install coaxial cable terminals in accordance with manufacturer's instructions.

### Install optical fibre terminals in accordance with manufacturer's instructions.

## INSTALLATION OF TELEPHONE CABLE ENTRANCE

### Colour match conductors on terminal strips to telephone authority standard.

### Use appropriate tool for connecting conductors to terminals.

END OF SECTION