# GENERAL

## System Description

### Data system includes data outlets and wiring for office and school applications.

### Data system equipment consists of:

#### Data outlets.

#### UTP cabling.

#### Patch Panels.

#### Patch Cords.

#### Line Cords.

#### Data Rack.

#### Conduit System.

#### System Switches

### Do not provide systems switches for school projects.  System switches provided under separate contract.

## Related sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 26 05 34 – Conduits, Conduit Fastenings and Conduit Fittings.

### Section 27 05 14 – Communication Cables – Inside Buildings.

### Section 27 05 28 – Pathways for Communications Systems.

### Section 27 10 05 – Structured Cabling for Communication Systems.

## REFERENCES

### Canadian Standards Association (CSA)

#### CAN/CSA-C22.2 No. 182.4, Plugs, Receptacles, and Connectors for Communication Systems.

#### CAN/CSAC-22.2 No. 214, Communications Cables.

### Electronic Industries Association (EIA)

#### EIA/TIA Bulletin TSB-36, Technical Systems Bulletin Additional Cable Specifications for Unshielded Twisted Pair Cables.

### Building Industry Consulting Services International (BICSI) Telecommunications Distribution Methods Manual (TDMM).

## SUBMITTALS

### Shop drawings to include the following items as minimum:

#### Outlets.

#### UTP Patch Panels.

#### Labels.

#### UTP Wire.

#### Data Rack.

#### Patch Cords.

#### Line Cords.

#### System switches

#### Cable Management Equipment

## Maintenance and operation

### Provide maintenance and operation data for incorporation in manual specified in Section 01 78 00 – Closeout Submittals.

## warranty

### Ensure each piece of equipment installed including wiring is warranted by the manufacturer to be free of defects in operation, material and workmanship for a period of 15 years from date of Substantial Completion.

# PRODUCTS

## OUTLETS

### Provide single or dual data outlet as indicated.

### Dual flush mounted data outlet.

#### Two 8 position RJ45 jacks with T568A (ISDN) wiring.

#### Two (2) blank inserts.

#### Colour: blue.

### Single flush mounted data outlets:

#### One (1) 8 position RJ45 jack with T586A (ISDN) wiring.

#### Three (3) blank inserts.

#### Color:  blue

## Cover Plates

### Provide flush mount type to accept four (4) modular data outlets.

### Indicate outlet number of “Data” cover plate.  Provide labeling as indicated and to Owner’s requirement.

### Color: grey.

### Construction: Themo – plastic.

## PATCH PANELS

### Modular (RJ45) style patch panels.

### Designed for high speed data, cross connect and interconnect specifications.

### 24 or 48 ports per panel suitable for modular jacks.

### Provide each port with a T568A (ISDN) eight pin jack as per par. 2.1 – outlets as necessary to accommodate number of runs.

### Designed for mounting in rack. Provide one horizontal cable manager for each 48 port patch panel.

### Retaining rings on panel to facilitate patch cord management.

### Provide patch panels in each data rack, quantity of panels as required to connect each data outlet to a corresponding patch panel port with a minimum of 10 spare ports.

## DATA RACKS

### Provide 480 x 2135 mm data racks in closet, free standing for installation of patch panels as indicated.

## Cable Management

### Cable management at data racks:

#### horizontal cable management channels, one for every 48 ports, five (5) per rack minimum.

#### Vertical cable management channels two (2) per rack.

### Cable management in accessible ceiling spaces:

#### Cable bundle support mounted to steel structure with beam clamps as required.  Support to be 50 mm diameter bridle ring.

#### Provide quantity as required to support all loose cables at 1000 mm spacings up to point of entry into zone conduit system.

#### Provide support for individual cables using caddy clip at 1000 mm spacings.

## PATCH AND   LINE CORDS

### Provide patch and line cords for connection of individual room equipment and for connection of Owner’s equipment in computer room.

### Provide 3 m long line cords.  24 gauge, solid conductor, category 6 T586A ISDN wired.

Quantity:  one per data outlet plus ten spares.

### Provide patch cords.  24 gauge, solid, conductor, category 6 T586A ISDN wired.   Quantity:  one per data outlet plus ten spares.  Provide 1/3 of quantity of 0.6 m long, 1/3 at 1.2 m long and 1/3 at 2.1 m long.

### Cords must be from same manufacturer as connectivity components.

### Patch cords must be factory assembled complete with connectors. Field assembled patch cables not acceptable.

## LABELS

### Provide indicating labels on UTP wiring and outlet assemblies.

### Labels to be:

#### Outlet identification labels.  Computer printable type:  indicating “Data Outlet”.

#### Labeling on wire from outlet to patch panel: heat shrink labels sized for data cables indicating data outlet # and port # on respective ends.

#### Coordinate labeling with Owner prior to fabrication.

## UTP WIRING

### 4 pair, 24 gauge, solid conductor, unshielded twisted pairs, CSA FT4 fire rating, Category 6, guaranteed for 2.4 Giga bytes per second transmission/receiving rate.

### Provide one cable from each single outlet back to patch panel (two cables from each duel data outlet back to patch panel).

## CONDUIT SYSTEMS

### Install conduit systems and pull boxes for data wiring including:

#### Vertical stubs in walls from outlets into accessible ceiling space.

#### Zone conduits as indicated on drawings for collection of UTP wiring in ceiling spaces.

#### Pull boxes.

## SYSTEM SWITCH

### Rack mounted, 48 port switch, full 10/100 Mbps and 2.4 Gbps data transmission rates, with two port fiber optic module for connection of fiber cables.

### Provide quantity of switches as required to provide one switched port for each horizontal cable terminating at data rack.

## Fibre Optic Components

### Provide 6 fiber, 50 micron, multimode rated fiber optic cable.

### Provide rack mounted patch panel with hinged fiber drawer and six (6) SC adapters.  Provide one at each end of fiber optic cables s indicated.

# PART 3 - EXECUTION

## INSTALLATION

### Install data system wiring and components.

### Install patch panels and switches in data racks at data closet locations as indicated.

### Terminate UTP and fiber optic cables at outlets and patch panel as indicated.  Ensure that the minimum number of twists per inch in the cable pairs is maintained at each connection point.

### Ensure that manufacturer’s bending radius limitations are adhered to.

### Protect cables from damage during installation.

### Zone conduits to be installed, as indicated, running back to patch panel location.

### Conduits to be run from data outlets to corridor ceiling space.  Provide insulated conduit bushing at open end of wall stub-up.

### Turn over UPT patch and line cords to Owner.

## CONDUIT SYSTEM RESTRICTIONS

### Do not provide conduit raceways that exceed 30 m or contain more than two 900 bends (or equivalent) between pull points or pull boxes.

### Do not provide pull boxes in lieu of conduit bends.

### LB connectors not permitted.

### Provide inside radius bends to a minimum of 6 times the internal diameter for conduits 50 mm and smaller.  For larger conduits provide inside radius bends to a minimum of 10 times the internal diameter of the conduit.

### Ensure conduits terminations are free from sharp edges and fitted with insulated bushings.

### Ream individual lengths of conduit to remove sharp edges.

### Provide sufficient conduit size to permit maximum 50% fill capacity.

## TESTING GENERAL

### Cabling and connectors to be tested by an experienced company employing trained technicians with minimum 5 years experience in data cabling industry. Experience to be acceptable to the Owner.

## TESTING UTP CABLING

### System to meet continuity and attenuation tests outlined in ANSI/TIA-568-C.2.

### Category 6 cable to meet ANSI standard ANSI/TIA-568-C.2 (capable of data transmission up to 2.4 G. bps).

### Perform system and channel tests after UTP cable installation o ensure that installation meets standard indicated above and values indicated in the IBDN design guide issue 2 (IBDN-DG-9202).  Tests to be performed using a Level IV tester. Minimum tests to be performed.

#### Continuity.

#### Attenuation.

#### Near and Crosstalk.

#### Resistance.

#### Pair Assignment Test.

#### Low Band Noise.

#### High Band Noise.

#### Mid Band Noise.

#### Length of Cable.

#### Return loss

#### ELFEXT

#### Propagation delay.

#### Deby skew.

Perform permanent link tests to cover all equipment wiring including patch panels and line cords. Perform tests from data closet outwards to data outlet line cord.

### Provide to construction manager written copy of the testing sequence to be performed, testing equipment to be used, and standards to which cable is being tested.

### Provide a written report to the Construction Manager indicating each cable tested and the results of the testing.  Provide printout from the Level IV tester for each cable.

### Replace cable and/or connection equipment that fails tests.

### Provide additional testing in accordance with Section 01 91 13.13 – Commissioning (Cx) Requirements.

END OF SECTION