# General

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 78 00 - Closeout Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 26 05 00 – Common Work Results - Electrical.

## SUBMITTALS

### Include riser diagram, talk paths of complete intercom, interphone system.

## CLOSEOUT SUBMITTALS

### Provide data for incorporation into maintenance manual specified in Sections 01 78 00 - Closeout Submittals.

### Include description of system operation.

### Include parts list using component identification numbers standard to electronics industry.

## SYSTEM START-UP

### Provide instructions in accordance with Section 26 05 00 – Common Work Results - Electrical.

## TRAINING

### Arrange and pay for on-site lectures and demonstrations by system manufacturer to train operational personnel in the use and maintenance of the system.

# Products

## MATERIALS

### Conduits: type EMT, size as indicated, in accordance with Section 26 05 00 – Common Work Results - Electrical.

### Communication conductors: type LVT, size as indicated, in accordance with Section 26 05 00 – Common Work Results - Electrical.

## MASTER STATIONS

### Electronic, desk or wall type as indicated for un- interrupted two-way voice communication.

### Digital pushbutton system including: hands free operation, talk back and conference facilities, electronic switchboard complete with power supply, amplifiers.

### Selector switch type, 16 station selector switches as indicated, and standby privacy switches.

#### Switches to have heavy duty cross bar palladium contacts.

### 16 annunciator lights, switch, and facilities, to call sub-stations simultaneously.

### Hand set: with carbon button transmitter and magnetic receiver for confidential conversations.

### Privacy, incoming call, in-use and busy lights.

### Audible signalling by soft electronic chimes.

### Manual noise free volume control.

### Built-in volume-matic circuit to automatically adjust incoming and outgoing volume levels.

### Switching components to have, operating life expectancy exceeding 5,000,000 cycles.

### Built-in transistorized amplifier: output power of 3-7 W with sensitivity of 93 dB.

### Speaker: built-in 100 mm dia.

### Power consumption: 30 mA at standby, 70 mA at full output from 24 V supply.

### Input and output line impedance: 80 ohms.

### Cabinet: die-cast finish colour to suit décor.

### Interconnects: plug and socket.

### Ventilation: natural convection.

## SUB-STATIONS

### Desk, Wall, Outdoor or Console type as indicated.

#### Facilities for hold-annunciator call origination to one master station.

#### Conversation between sub-stations not possible.

#### Signalling automatically sounds soft chime to indicate incoming calls.

#### Call origination switch, with palladium contacts, illuminated privacy indicator, printact relay, volume control, transformer and housing.

#### Speaker: 100 mm diametre 93 dB sensitivity, with permanent magnet of 20 g.

#### Rugged wire wound volume control to adjust incoming volume level.

#### Housing: die cast with beige colour baked enamel finish.

## POWER SUPPLY

### Power supply unit, for selector switch type system, well filtered, regulated, constant voltage under load.

#### Output: 24 V DC at 2 A.

#### Input: 110-120 V, 60 Hz.

#### Power consumption: 50 W.

#### Fuse: 2 A, replaceable.

#### Rectifier: silicon full wave bridge.

#### Filter, choke and dual capacitors.

#### Hook-up, (+) (-) terminal strip with terminal screws.

#### Line cord: 2 m, 3 conductor with specially constructed strain relief.

#### Housing: metal case.

#### Finish: metallic paint, colour standard.

## ADDITIONAL FEATURES

### Interface with pocket paging system.

# Execution

## INSTALLATION

### Install equipment as indicated and in accordance with manufacturer's instructions.

### Interconnect system components.

## Field Quality Control

### Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Conduct intelligibility performance test.

END OF SECTION